## EXTERNAL WALL LOAD
EXTERNAL WALL LOAD
FIRST FLOOR
Space | Orientation | U | A(m^2) | CLTDsel | LM | k | Ti | Tave | CLTD adj | Q(W) |  | Summary of Data
Power House | E | 2.7144 | 22 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 1492.92 |  |  | Q
Power House | N | 2.7144 | 16 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 564.5952 |  | FIRST FLOOR | 39227.8573
Maintenance Office | N | 2.7144 | 5.8 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 204.6658 |  | SECOND FLOOR | 31364.0949
Maintenance Office CR | N | 2.7144 | 5.04 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 177.8475 |  | THIRD FLOOR | #NAME?
Female Toilet | N | 2.7144 | 11.28 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 398.0396 |  | TOTAL | #NAME?
Male Toilet | N | 2.7144 | 11.28 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 398.0396
MINOR OPERATING ROOM | N | 2.7144 | 13.6 | 13 | 2.22 | 0.65 | 22 | 30.45 | 14.343 | 479.9059
Examination/Treatment AREA | N | 2.7144 | 19.6 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 691.6291
Examination/Treatment AREA | W | 2.7144 | 29.6 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 2651.4259
CR | N | 2.7144 | 8.08 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 285.1206
Cadaver Holding Room | E | 2.7144 | 22.4 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 1520.064
EMERGENCY ROOM | W | 2.7144 | 23.6 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 2113.9747
HALLWAY | W | 2.7144 | 49.85 | 33 | -0.55 | 0.65 | 28 | 30.45 | 19.5425 | 4465.3237
Work Area (laboratory) | E | 2.7144 | 21.6 | 25 | -0.55 | 0.65 | 22 | 30.45 | 20.3425 | 1465.776
WAITING AREA (CR) | E | 2.7144 | 6.12 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 415.3032
Film File Storage | E | 2.7144 | 6.04 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 409.8744
Pressing Area | E | 2.7144 | 10 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 678.6
Ultrasound | N | 2.7144 | 5.24 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 184.9049
Ultrasound | W | 2.7144 | 19.2 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 1719.8438
Ultrasound CR | N | 2.7144 | 6.4 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 225.8381
Ultrasound CR | W | 2.7144 | 7.04 | 33 | -0.55 | 0.65 | 24 | 30.45 | 23.5425 | 630.6094
Cooking Area | S | 2.7144 | 12.52 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 747.6543
Cooking Area | E | 2.7144 | 19.8 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 1343.628
Dietician's Office | S | 2.7144 | 11.6 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 692.7149
Dietician's Office CR | S | 2.7144 | 5.6 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 334.4141
Staff Dining | S | 2.7144 | 26.12 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 1559.8028
OPD clinic Ob-gyne | W | 2.7144 | 10.64 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 953.0801
OPD clinic Ob-gyne | S | 2.7144 | 19.4 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 1158.5059
CR | W | 2.7144 | 6.4 | 33 | -0.55 | 0.65 | 24 | 30.45 | 23.5425 | 573.2813
CR | S | 2.7144 | 6.84 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 408.4629
Canteen | W | 2.7144 | 39.2 | 33 | -0.55 | 0.65 | 24 | 30.45 | 23.5425 | 3511.3478
Canteen | E | 2.7144 | 44.8 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 3040.128
Canteen | S | 2.7144 | 50.8 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 3033.6134
Washing Area | E | 2.7144 | 10.27 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 696.9222
[9 empty] | Total Load: | 39227.8573
SECOND FLOOR
Space | Orientation | U | A(m^2) | CLTDsel | LM | k | Ti | Tave | CLTD adj | Q(W)
5 Bed Ward E | E | 2.7144 | 26 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 1400.3725
5 Bed Ward N | N | 2.7144 | 19.38 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 728.212
5 Bed Ward | N | 2.7144 | 19.38 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 728.212
Stairs N | N | 2.7144 | 43.2 | 13 | 2.22 | 0.65 | 28 | 30.45 | 8.343 | 978.3175
Stairs W | W | 2.7144 | 41.2 | 33 | -0.55 | 0.65 | 28 | 30.45 | 19.5425 | 2185.5019
5-Bed Ward | N | 2.7144 | 19.38 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 728.212
5-Bed Ward N | N | 2.7144 | 19.38 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 728.212
5-Bed Ward W | W | 2.7144 | 26 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 1767.3594
Hallway (W) | W | 2.7144 | 9.7 | 33 | -0.55 | 0.65 | 28 | 30.45 | 19.5425 | 514.5478
Isolation room W | W | 2.7144 | 12.28 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 834.7374
Isolation room S | S | 2.7144 | 10.48 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 447.413
Isolation room CR | W | 2.7144 | 7.48 | 33 | -0.55 | 0.65 | 24 | 30.45 | 23.5425 | 478.0001 | 8.2
Private Room | W | 2.7144 | 9 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 611.7783
Private Room | W | 2.7144 | 9 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 611.7783
Private Room | W | 2.7144 | 9 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 611.7783
Private Room | W | 2.7144 | 9 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 611.7783
CSSR | W | 2.7144 | 13.05 | 33 | -0.55 | 0.65 | 24 | 30.45 | 23.5425 | 833.9441 | 15
Sterile Supply Room N | N | 2.7144 | 12 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 402.0461
Sterile Supply Room W | W | 2.7144 | 10.58 | 33 | -0.55 | 0.65 | 24 | 30.45 | 23.5425 | 676.1018 | 15.6
Recovery Room W | W | 2.7144 | 30.4 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 2066.451
Recovery Room S | S | 2.7144 | 21.6 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 922.149 | 24
Recovery Room CR | S | 2.7144 | 4.44 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 171.4749 | 4.8
Hallway (S) | S | 2.7144 | 19.2 | 22 | -3.88 | 0.65 | 28 | 30.45 | 10.228 | 533.0474
Lounge Area | S | 2.7144 | 21.2 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 905.0722 | 5.4
DR-1 | S | 2.7144 | 5.04 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 215.1681
DR-2 | S | 2.7144 | 5.04 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 215.1681
DR-3 | S | 2.7144 | 5.04 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 215.1681
Anesthesia Off. And Storage | S | 2.7144 | 9.8 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 378.4807 | 11.4
Sterile Storage | S | 2.7144 | 8.8 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 339.8603 | 10.4
Clean-up Room | S | 2.7144 | 10.4 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 401.653 | 12
Sub-Ster Room | S | 2.7144 | 10.4 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 443.9977
Major Operating Room S | S | 2.7144 | 24 | 22 | -3.88 | 0.65 | 22 | 30.45 | 16.228 | 1057.1828
Major Operating Room E | E | 2.7144 | 24 | 25 | -0.55 | 0.65 | 22 | 30.45 | 20.3425 | 1325.2244
Fire Exit | E | 2.7144 | 7.4 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 398.5676
Delivery Room E | E | 2.7144 | 24 | 25 | -0.55 | 0.65 | 22 | 30.45 | 20.3425 | 1325.2244
Delivery Room N | N | 2.7144 | 9.4 | 13 | 2.22 | 0.65 | 22 | 30.45 | 14.343 | 365.9668 | 15
Chief of Clinics | E | 2.7144 | 12.9 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 694.8002
Conference Room | E | 2.7144 | 20.4 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 1098.7538 | 24.2
Chief of Hospital | E | 2.7144 | 8.16 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 439.5015 | 10.88
Reception (CR) | E | 2.7144 | 10.2 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 507.8466 | 10.92
Isolation Room S | S | 2.7144 | 12.28 | 22 | -0.55 | 0.65 | 22.5 | 30.45 | 17.8925 | 596.4077
Isolation Room E | E | 2.7144 | 8.88 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 478.2811 | 10.28
Isolation Room CR | E | 2.7144 | 7.84 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 390.3448 | 8.2
[9 empty] | Total Load: | 31364.0949
THIRD FLOOR
Space | Orientation | U | A(m^2) | CLTDsel | LM | k | Ti | Tave | CLTD adj | Q(W)
5 Bed Ward E | E | 2.7144 | 26 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
5 Bed Ward N | N | 2.7144 | 19.4 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME? | 24.02
5 Bed Ward | N | 2.7144 | 19.4 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME? | 24.02
Stairs E | E | 2.7144 | 40.92 | #NAME? | #NAME? | 0.65 | 28 | 30.45 | #NAME? | #NAME?
Stairs N | N | 2.7144 | 68 | #NAME? | #NAME? | 0.65 | 28 | 30.45 | #NAME? | #NAME?
Stairs W | W | 2.7144 | 40.92 | #NAME? | #NAME? | 0.65 | 28 | 30.45 | #NAME? | #NAME?
5 Bed Ward | N | 2.7144 | 19.4 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
5 Bed Ward N | N | 2.7144 | 19.4 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
5 Bed Ward W | W | 2.7144 | 26 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
Hallway | W | 2.7144 | 9.7 | #NAME? | #NAME? | 0.65 | 28 | 30.45 | #NAME? | #NAME?
Isolation Room W | W | 2.7144 | 13.4 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
Isolation Room CR | W | 2.7144 | 8.56 | #NAME? | #NAME? | 0.65 | 24 | 30.45 | #NAME? | #NAME? | 8.92
Isolation Room S | S | 2.7144 | 12 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
Private Room | W | 2.7144 | 10.6 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
Private Room | W | 2.7144 | 10.6 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
Private Room | W | 2.7144 | 10.6 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
Private Room | W | 2.7144 | 10.6 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
Solarium | W | 2.7144 | 11.65 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME? | 15
Admitting N | N | 2.7144 | 12 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
Admitting W | W | 2.7144 | 13.2 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
Billing | W | 2.7144 | 13.2 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
Cashier | W | 2.7144 | 10.4 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
Personel's Dining W | W | 2.7144 | 7.69 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME? | 9.92
Personel's Dining CR W | W | 2.7144 | 7.16 | #NAME? | #NAME? | 0.65 | 24 | 30.45 | #NAME? | #NAME? | 7.52
Personel's Dining CR S | S | 2.7144 | 6 | #NAME? | #NAME? | 0.65 | 24 | 30.45 | #NAME? | #NAME?
Personel's Dining S | S | 2.7144 | 20.4 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME? | 22.8
Stairs S | S | 2.7144 | 19.2 | #NAME? | #NAME? | 0.65 | 28 | 30.45 | #NAME? | #NAME?
Female Toilet | S | 2.7144 | 11.28 | #NAME? | #NAME? | 0.65 | 24 | 30.45 | #NAME? | #NAME?
Male Toilet | S | 2.7144 | 11.28 | #NAME? | #NAME? | 0.65 | 24 | 30.45 | #NAME? | #NAME? | 12
Hallway S | S | 2.7144 | 24 | #NAME? | #NAME? | 0.65 | 28 | 30.45 | #NAME? | #NAME?
Water Tank S | S | 2.7144 | 48 | #NAME? | #NAME? | 0.65 | 24 | 30.45 | #NAME? | #NAME?
Water Tank E | E | 2.7144 | 61.6 | #NAME? | #NAME? | 0.65 | 24 | 30.45 | #NAME? | #NAME?
Water Tank N | N | 2.7144 | 8.88 | #NAME? | #NAME? | 0.65 | 24 | 30.45 | #NAME? | #NAME?
Solarium | E | 2.7144 | 11.67 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME? | 15
Private Room | E | 2.7144 | 10.6 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
Private Room | E | 2.7144 | 10.6 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
Private Room | E | 2.7144 | 10.6 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
Private Room | E | 2.7144 | 10.6 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
Isolation Room S | S | 2.7144 | 8.88 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
Isolation Room E | E | 2.7144 | 13.4 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME? | 14.8
Isolation Room CR | E | 2.7144 | 9.04 | #NAME? | #NAME? | 0.65 | 24 | 30.45 | #NAME? | #NAME? | 9.4
Fire Exit | E | 2.7144 | 7.4 | #NAME? | #NAME? | 0.65 | 22.5 | 30.45 | #NAME? | #NAME?
[9 empty] | Total Load | #NAME?

## GLASS LOAD
GLASS LOAD
FIRST FLOOR
Space | Orientation | U | To | Ti | A(m^2) | SHGF | SCL | SC | Qsg (W) | Qth (W) |  | Summary of Data
Power House | E | 2.8722 | 34.5 | 22.5 | 4 | #NAME? | #NAME? | 0.55 | #NAME? | 137.8656 |  |  | QS | QL | Q
Maintenance Office | N | 2.8722 | 34.5 | 22.5 | 1.2 | #NAME? | #NAME? | 0.55 | #NAME? | 41.3597 |  | FIRST FLOOR | #NAME? | 2026.9213 | #NAME?
Maintenance Office CR | N | 2.8722 | 34.5 | 24 | 0.36 | #NAME? | #NAME? | 0.55 | #NAME? | 10.8569 |  | SECOND FLOOR | #NAME? | 2185.8239 | #NAME?
Famale Toilet | N | 2.8722 | 34.5 | 24 | 0.72 | #NAME? | #NAME? | 0.55 | #NAME? | 21.7138 |  | THIRD FLOOR | #NAME? | 1551.1017 | #NAME?
Male Toilet | N | 2.8722 | 34.5 | 24 | 0.72 | #NAME? | #NAME? | 0.55 | #NAME? | 21.7138 |  | TOTAL | #NAME? | 5763.8469 | #NAME?
Minor Operating Room | N | 2.8211 | 34.5 | 22 | 1.6 | #NAME? | #NAME? | 0.55 | #NAME? | 56.422
Exaination/Treatment and Obs Area | N | 2.8722 | 34.5 | 22.5 | 4.4 | #NAME? | #NAME? | 0.55 | #NAME? | 151.6522
Exaination/Treatment and Obs Area CR | N | 2.8722 | 34.5 | 22.5 | 0.72 | #NAME? | #NAME? | 0.55 | #NAME? | 24.8158
Emergency Room | W | 2.8722 | 34.5 | 22.5 | 2 | #NAME? | #NAME? | 0.55 | #NAME? | 68.9328
Hallway | W | 2.8722 | 34.5 | 28 | 2.75 | #NAME? | #NAME? | 0.55 | #NAME? | 51.3406
Hallway | W | 2.8211 | 34.5 | 28 | 9 | #NAME? | #NAME? | 0.55 | #NAME? | 165.0344
Ultrasound N | N | 2.8722 | 34.5 | 22.5 | 0.6 | #NAME? | #NAME? | 0.55 | #NAME? | 20.6798
Ultrasound W | W | 2.8722 | 34.5 | 22.5 | 4.2 | #NAME? | #NAME? | 0.55 | #NAME? | 144.7589
Ultrasound CR | W | 2.8722 | 34.5 | 24 | 0.36 | #NAME? | #NAME? | 0.55 | #NAME? | 10.8569 | Awning or Sliding | 2.8722
OPB Clinic OB-Gyne W | W | 2.8722 | 34.5 | 22.5 | 0.6 | #NAME? | #NAME? | 0.55 | #NAME? | 20.6798 | Fixed | 2.8211
OPB Clinic OB-Gyne S | S | 2.8722 | 34.5 | 22.5 | 1.6 | #NAME? | #NAME? | 0.55 | #NAME? | 55.1462
OPB Clinic OB-Gyne CR | S | 2.8722 | 34.5 | 24 | 0.36 | #NAME? | #NAME? | 0.55 | #NAME? | 10.8569
Canteen W | W | 2.8722 | 34.5 | 24 | 4.2 | #NAME? | #NAME? | 0.55 | #NAME? | 126.664
Canteen S | S | 2.8722 | 34.5 | 24 | 8.4 | #NAME? | #NAME? | 0.55 | #NAME? | 253.328
Canteen E | E | 2.8722 | 34.5 | 24 | 1.4 | #NAME? | #NAME? | 0.55 | #NAME? | 42.2213
Dietary | S | 2.8722 | 34.5 | 22.5 | 2.4 | #NAME? | #NAME? | 0.55 | #NAME? | 82.7194
Dietitian Office | S | 2.8722 | 34.5 | 22.5 | 2.8 | #NAME? | #NAME? | 0.55 | #NAME? | 96.5059
Cooking Area S | S | 2.8722 | 34.5 | 24 | 1.8 | #NAME? | #NAME? | 0.55 | #NAME? | 54.2846
Cooking Area E | E | 2.8722 | 34.5 | 24 | 2.4 | #NAME? | #NAME? | 0.55 | #NAME? | 72.3794
Washing Area | E | 2.8722 | 34.5 | 24 | 1.73 | #NAME? | #NAME? | 0.55 | #NAME? | 52.1735
Pressing Area | E | 2.8722 | 34.5 | 22.5 | 2 | #NAME? | #NAME? | 0.55 | #NAME? | 68.9328
Film File Storage | E | 2.8722 | 34.5 | 24 | 0.36 | #NAME? | #NAME? | 0.55 | #NAME? | 10.8569
Waiting Area CR | E | 2.8722 | 34.5 | 24 | 0.36 | #NAME? | #NAME? | 0.55 | #NAME? | 10.8569
Work Area Laboratory | E | 2.8722 | 34.5 | 22 | 2.4 | #NAME? | #NAME? | 0.55 | #NAME? | 86.166
Cadaver Holding Room | E | 2.8722 | 34.5 | 22.5 | 1.6 | #NAME? | #NAME? | 0.55 | #NAME? | 55.1462
[7 empty] | Total: |  | #NAME? | 2026.9213
[7 empty] | Overall Total Load: |  | #NAME?
SECOND FLOOR
Space | Orientation | U | To | Ti | A(m^2) | SHGF | SCL | SC | Qsg (W) | Qth (W)
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 4.62 | #NAME? | #NAME? | 0.55 | #NAME? | 159.2348
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 4.62 | #NAME? | #NAME? | 0.55 | #NAME? | 159.2348
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 4.62 | #NAME? | #NAME? | 0.55 | #NAME? | 159.2348
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 4.62 | #NAME? | #NAME? | 0.55 | #NAME? | 159.2348
Hallway | W | 2.8211 | 34.5 | 28 | 2.7 | #NAME? | #NAME? | 0.55 | #NAME? | 49.5103
Isolation Room | W | 2.8722 | 34.5 | 22.5 | 1.4 | #NAME? | #NAME? | 0.55 | #NAME? | 48.253
Isolation Room CR | W | 2.8722 | 34.5 | 24 | 0.36 | #NAME? | #NAME? | 0.55 | #NAME? | 10.8569
Private Room | W | 2.8722 | 34.5 | 22.5 | 3 | #NAME? | #NAME? | 0.55 | #NAME? | 103.3992
Private Room | W | 2.8722 | 34.5 | 22.5 | 3 | #NAME? | #NAME? | 0.55 | #NAME? | 103.3992
Private Room | W | 2.8722 | 34.5 | 22.5 | 3 | #NAME? | #NAME? | 0.55 | #NAME? | 103.3992
Private Room | W | 2.8722 | 34.5 | 22.5 | 3 | #NAME? | #NAME? | 0.55 | #NAME? | 103.3992
CSSR | W | 2.8722 | 34.5 | 22.5 | 1.95 | #NAME? | #NAME? | 0.55 | #NAME? | 67.2095
Sterile Supply Room | W | 2.8722 | 34.5 | 24 | 5.02 | #NAME? | #NAME? | 0.55 | #NAME? | 151.3937
Recovery Room | S | 2.8722 | 34.5 | 22.5 | 2.4 | #NAME? | #NAME? | 0.55 | #NAME? | 82.7194
Recovery Room CR | S | 2.8722 | 34.5 | 24 | 0.36 | #NAME? | #NAME? | 0.55 | #NAME? | 10.8569
Lounge Area | S | 2.8722 | 34.5 | 22.5 | 2.8 | #NAME? | #NAME? | 0.55 | #NAME? | 96.5059
DR 1 | S | 2.8722 | 34.5 | 24 | 0.36 | #NAME? | #NAME? | 0.55 | #NAME? | 10.8569
DR 2 | S | 2.8722 | 34.5 | 24 | 0.36 | #NAME? | #NAME? | 0.55 | #NAME? | 10.8569
DR 3 | S | 2.8722 | 34.5 | 24 | 0.36 | #NAME? | #NAME? | 0.55 | #NAME? | 10.8569
Anesthesia Off. and Storage | S | 2.8722 | 34.5 | 24 | 1.6 | #NAME? | #NAME? | 0.55 | #NAME? | 48.253
Sterile Storage | S | 2.8722 | 34.5 | 24 | 1.6 | #NAME? | #NAME? | 0.55 | #NAME? | 48.253
Clean-up Room | S | 2.8722 | 34.5 | 24 | 1.6 | #NAME? | #NAME? | 0.55 | #NAME? | 48.253
Sub-Ster Room | S | 2.8722 | 34.5 | 22.5 | 1.6 | #NAME? | #NAME? | 0.55 | #NAME? | 55.1462
Chief of Clinics | E | 2.8722 | 34.5 | 22.5 | 2.1 | #NAME? | #NAME? | 0.55 | #NAME? | 72.3794
Conference Room | E | 2.8722 | 34.5 | 22.5 | 3.6 | #NAME? | #NAME? | 0.55 | #NAME? | 124.079
Chief of Hospital | E | 2.8722 | 34.5 | 22.5 | 2.72 | #NAME? | #NAME? | 0.55 | #NAME? | 93.7486
Reception (CR) | S | 2.8722 | 34.5 | 24 | 1.2 | #NAME? | #NAME? | 0.55 | #NAME? | 36.1897
Isolation Room | E | 2.8722 | 34.5 | 22.5 | 1.4 | #NAME? | #NAME? | 0.55 | #NAME? | 48.253
Isolation Room CR | E | 2.8722 | 34.5 | 24 | 0.36 | #NAME? | #NAME? | 0.55 | #NAME? | 10.8569
[7 empty] | Total: |  | #NAME? | 2185.8239
[7 empty] | Overall Total Load |  | #NAME?
THIRD FLOOR
Space | Orientation | U | To | Ti | A(m^2) | SHGF | SCL | SC | Qsg (W) | Qth (W)
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 2.31 | #NAME? | #NAME? | 0.55 | #NAME? | 79.6174
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 2.31 | #NAME? | #NAME? | 0.55 | #NAME? | 79.6174
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 2.31 | #NAME? | #NAME? | 0.55 | #NAME? | 79.6174
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 2.31 | #NAME? | #NAME? | 0.55 | #NAME? | 79.6174
Hallway | W | 2.8722 | 34.5 | 28 | 2.7 | #NAME? | #NAME? | 0.55 | #NAME? | 50.4071
Isolation Room | W | 2.8722 | 34.5 | 22.5 | 1.4 | #NAME? | #NAME? | 0.55 | #NAME? | 48.253
Private Room | W | 2.8722 | 34.5 | 22.5 | 1.4 | #NAME? | #NAME? | 0.55 | #NAME? | 48.253
Private Room | W | 2.8722 | 34.5 | 22.5 | 1.4 | #NAME? | #NAME? | 0.55 | #NAME? | 48.253
Private Room | W | 2.8722 | 34.5 | 22.5 | 1.4 | #NAME? | #NAME? | 0.55 | #NAME? | 48.253
Private Room | W | 2.8722 | 34.5 | 22.5 | 1.4 | #NAME? | #NAME? | 0.55 | #NAME? | 48.253
Solarium | W | 2.8211 | 34.5 | 22.5 | 3.35 | #NAME? | #NAME? | 0.55 | #NAME? | 113.4082
Admitting | W | 2.8722 | 34.5 | 22.5 | 2.4 | #NAME? | #NAME? | 0.55 | #NAME? | 82.7194
Billing | W | 2.8722 | 34.5 | 22.5 | 2.4 | #NAME? | #NAME? | 0.55 | #NAME? | 82.7194
Cashier | W | 2.8722 | 34.5 | 22.5 | 2.4 | #NAME? | #NAME? | 0.55 | #NAME? | 82.7194
Personel's Dining W | W | 2.8722 | 34.5 | 22.5 | 2.23 | #NAME? | #NAME? | 0.55 | #NAME? | 76.8601
Personel's Dining CR | W | 2.8722 | 34.5 | 24 | 0.36 | #NAME? | #NAME? | 0.55 | #NAME? | 10.8569
Personel's Dining S | S | 2.8722 | 34.5 | 22.5 | 2.4 | #NAME? | #NAME? | 0.55 | #NAME? | 82.7194
Female Toilet | S | 2.8722 | 34.5 | 24 | 0.72 | #NAME? | #NAME? | 0.55 | #NAME? | 21.7138
Male Toilet | S | 2.8722 | 34.5 | 24 | 0.72 | #NAME? | #NAME? | 0.55 | #NAME? | 21.7138
Solarium | E | 2.8211 | 34.5 | 22.5 | 3.35 | #NAME? | #NAME? | 0.55 | #NAME? | 113.4082
Private Room | E | 2.8722 | 34.5 | 22.5 | 1.4 | #NAME? | #NAME? | 0.55 | #NAME? | 48.253
Private Room | E | 2.8722 | 34.5 | 22.5 | 1.4 | #NAME? | #NAME? | 0.55 | #NAME? | 48.253
Private Room | E | 2.8722 | 34.5 | 22.5 | 1.4 | #NAME? | #NAME? | 0.55 | #NAME? | 48.253
Private Room | E | 2.8722 | 34.5 | 22.5 | 1.4 | #NAME? | #NAME? | 0.55 | #NAME? | 48.253
Isolation Room | E | 2.8722 | 34.5 | 22.5 | 1.4 | #NAME? | #NAME? | 0.55 | #NAME? | 48.253
Isolation Room CR | E | 2.8722 | 34.5 | 24 | 0.36 | #NAME? | #NAME? | 0.55 | #NAME? | 10.8569
[7 empty] | Total: |  | #NAME? | 1551.1017
[7 empty] | Overall Total Load |  | #NAME?

## INFILTRATION LOAD
INFILTRATION LOAD
FIRST FLOOR
SPACE | Volume | L/s | To | Ti | Wo | Wi | Qs (W) | Ql (W) |  | Summary of Data
1.1 Power House | 149.7544 | 10.982 | 34.5 | 22.5 | 0.018137 | 0.0092932 | 162.3577 | 291.3582 |  |  | QS | QL | Q
1.2 Work Area | 38.6048 | 2.831 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 41.8538 | 82.0102 |  | FIRST FLOOR | 6335.2156 | 13463.2217 | 19798.4374
1.3 Storage Room | 31.27 | 2.2019 | 34.5 | 24 | 0.018137 | 0.0092932 | 28.4842 | 58.4184 |  | SECOND FLOOR | 5646.477 | #NAME? | #NAME?
1.4 Maintenance Office | 65.238 | 4.7841 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 70.7284 | 138.5884 |  | THIRD FLOOR | 5262.1037 | #NAME? | #NAME?
1.4 Maintenance Office CR | 11.35 | 0.79923 | 34.5 | 24 | 0.018137 | 0.0092932 | 10.3388 | 21.204 |  | TOTAL | 17243.7963 | #NAME? | #NAME?
1.5 Female toilet | 73.1964 | 5.1542 | 34.5 | 24 | 0.018137 | 0.0092932 | 66.6753 | 136.745
1.6 Male Toilet | 73.3856 | 5.1676 | 34.5 | 24 | 0.018137 | 0.0092932 | 66.8477 | 137.0985
1.7 Minor Operating Room | 93.5544 | 6.9516 | 34.5 | 22 | 0.018137 | 0.0082198 | 107.0548 | 206.8172
1.8 Equipment and supply storage area | 22.44 | 1.5802 | 34.5 | 24 | 0.018137 | 0.0092932 | 20.4408 | 41.9223
1.9 Emergency Room | 525.2 | 38.5147 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 569.4008 | 1115.7093
1.9 Examination/Treatment Area CR | 14.8348 | 1.0446 | 34.5 | 24 | 0.018137 | 0.0092932 | 13.5132 | 27.7143
1.10 Cadaver Holding Room | 78.5512 | 5.7604 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 85.1621 | 166.8703
1.11 Supply Room | 125.1572 | 9.1782 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 135.6904 | 265.8779
1.12 Bulk Storage | 15.9088 | 1.1202 | 34.5 | 24 | 0.018137 | 0.0092932 | 14.4915 | 29.7207
1.13 Pharmacy | 82.9948 | 6.0863 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 89.9796 | 176.3101
1.14 Medical Records Office | 71.8048 | 5.2657 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 77.8479 | 152.5386
1.15 Medical Records | 74.5232 | 5.465 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 80.7951 | 158.3135
1.16 PHILHEALTH | 68.5512 | 5.0271 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 74.3205 | 145.6268
1.17 Doctor's Duty | 46.4248 | 3.4045 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 50.3319 | 98.6226
1.18 Nurse Station (ER) CR | 11.9092 | 0.83861 | 34.5 | 24 | 0.018137 | 0.0092932 | 10.8482 | 22.2487
HALLWAY | 2624.716 | 164.4093 | 34.5 | 28 | 0.018137 | 0.011816 | 1316.5896 | 3117.4609 | 656.179
1.21 Work Area (laboratory) | 131.44 | 9.7667 | 34.5 | 22 | 0.018137 | 0.0082198 | 150.4075 | 290.5695
1.23 Waiting area | 50.71 | 3.7187 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 54.9778 | 107.7259
1.23 Waiting area CR | 12.9452 | 0.91156 | 34.5 | 24 | 0.018137 | 0.0092932 | 11.7919 | 24.1841
1.24 OPD clinic dental 1 | 57.5244 | 4.2185 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.3657 | 122.202
1.25 OPD clinic dental 2 | 57.5244 | 4.2185 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.3657 | 122.202
1.26 Elevator | 35.8604 | 2.6298 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 38.8784 | 76.1801
1.27 OPD clinic surgery 1 | 57.7424 | 4.2344 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.602 | 122.6651
1.28 OPD clinic surgery 2 | 57.7424 | 4.2344 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.602 | 122.6651
1.29 Cashier | 21.95 | 1.6097 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 23.7973 | 46.6295
1.30 Billing | 22.04 | 1.6163 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 23.8949 | 46.8207
1.31 Admitting | 22.5452 | 1.6533 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 24.4426 | 47.8939
1.32 Film File Storage | 22.0812 | 1.5549 | 34.5 | 24 | 0.018137 | 0.0092932 | 20.114 | 41.2519
1.33 Radiologist Office | 36.5968 | 2.6838 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 39.6768 | 77.7445
1.34 Dark Room | 19.8088 | 1.4526 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 21.4759 | 42.0808
1.35 Control Booth | 101.0152 | 7.4078 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 109.5166 | 214.5918
1.37 OPD Clinic Pedia 1 | 57.5244 | 4.2185 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.3657 | 122.202
1.38 OPD Clinic Pedia 2 | 57.5244 | 4.2185 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.3657 | 122.202
1.39 OPD Records | 41.672 | 3.0559 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 45.1791 | 88.526
1.40 OPD info. And admitting | 39.922 | 2.9276 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 43.2818 | 84.8084
1.41 OPD Clinic Medical 1 | 57.7424 | 4.2344 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.602 | 122.6651
1.42 OPD Clinic Medical 2 | 57.7424 | 4.2344 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.602 | 122.6651
1.46 Pressing Area | 33.724 | 2.4731 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.5622 | 71.6416
1.47 Linen Storage | 33.2548 | 2.3417 | 34.5 | 24 | 0.018137 | 0.0092932 | 30.2921 | 62.1264
1.49 Linen Office | 33.75 | 2.3766 | 34.5 | 24 | 0.018137 | 0.0084806 | 30.7432 | 68.8453
1.50 Admin Office | 54.428 | 3.9914 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 59.0087 | 115.6242
1.51 Male Toilet | 69.0396 | 4.8615 | 34.5 | 24 | 0.018137 | 0.0092932 | 62.8889 | 128.9793
1.53 Washing Area | 68.5068 | 5.0238 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 74.2723 | 145.5325
1.54 Receiving Sorting Area | 34.2844 | 2.5142 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 37.1698 | 72.8321
1.55 Administrative office | 141.2708 | 10.3599 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 153.1602 | 300.1088
1.56 Social Welfare | 54.3936 | 3.9889 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 58.9714 | 115.5511
1.57 Female Toilet | 68.1712 | 4.8004 | 34.5 | 24 | 0.018137 | 0.0092932 | 62.0978 | 127.357
1.58 OPD Info. And admitting | 41.7668 | 3.0629 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 45.2819 | 88.7274
1.59 OPD records | 46.3676 | 3.4003 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 50.2699 | 98.5011
1.60 Ultrasound | 76.3076 | 5.5959 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 82.7296 | 162.1041
1.60 Ultrasound CR | 10.1376 | 0.71386 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.2344 | 18.939
1.61 Cooking Area | 136.8608 | 9.6373 | 34.5 | 24 | 0.018137 | 0.0092932 | 124.6679 | 255.6824
1.62 Dry storage | 10.3764 | 0.73067 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.452 | 19.3851
1.63 Cold Storage | 7.85 | 0.55277 | 34.5 | 24 | 0.018137 | 0.0092932 | 7.1506 | 14.6653
1.64 Supply Receiving Area | 22.8736 | 1.6774 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 24.7986 | 48.5916
1.65 Dietician's Office | 36.9 | 2.706 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 40.0055 | 78.3886
1.65 Dietician's Office CR | 7.78 | 0.54784 | 34.5 | 24 | 0.018137 | 0.0092932 | 7.0869 | 14.5345
1.66 Dietary | 152.13 | 10.7125 | 34.5 | 24 | 0.018137 | 0.0084806 | 138.5767 | 310.3239
1.67 Staff Dining | 203.5524 | 14.3335 | 34.5 | 24 | 0.018137 | 0.0084806 | 185.4179 | 415.2184
1.68 OPD clinic Ob-gyne | 108.0224 | 7.9216 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 117.1136 | 229.4775
1.68 OPD clinic Ob-gyne CR | 10.1376 | 0.71386 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.2344 | 18.939
1.70 Canteen | 726.7968 | 51.1786 | 34.5 | 24 | 0.018137 | 0.0092932 | 662.0465 | 1357.7967
X Ray CR | 7.8824 | 0.55505 | 34.5 | 24 | 0.018137 | 0.0092932 | 7.1802 | 14.7258
Washing Area CR | 9.6 | 0.676 | 34.5 | 24 | 0.18137 | 0.0092932 | 8.7447 | 348.9717
[5 empty] | Total |  | 6335.2156 | 13463.2217
[5 empty] | Total Load |  | 19798.4374
SECOND FLOOR
SPACE | Volume | L/s | To | Ti | Wo | Wi | Qs (W) | Ql (W)
5-Bed Ward 1 | 137.1076 | 10.0546 | 34.5 | 22.5 | 0.018137 | #NAME? | 148.4053 | #NAME?
5-Bed Ward 1 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5217 | #NAME?
5-Bed Ward 2 | 137.04 | 10.0496 | 34.5 | 22.5 | 0.018137 | #NAME? | 148.3321 | #NAME?
5-Bed Ward 2 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5217 | #NAME?
Hallway 1 | 881.3296 | 55.2055 | 34.5 | 28 | 0.018137 | #NAME? | 441.368 | #NAME? | 707.7447
Hallway 2 | 573.1645 | 35.9024 | 34.5 | 28 | 0.018137 | #NAME? | 287.0396 | #NAME?
Hallway 3 | 315.0296 | 19.7331 | 34.5 | 28 | 0.018137 | #NAME? | 157.7662 | #NAME?
Hallway 4 | 398.6188 | 24.969 | 34.5 | 28 | 0.018137 | #NAME? | 199.6275 | #NAME?
Hallway 5 | 571.5204 | 35.7994 | 34.5 | 28 | 0.018137 | #NAME? | 286.2162 | #NAME?
5-Bed Ward 3 | 137.16 | 10.0584 | 34.5 | 22.5 | 0.018137 | #NAME? | 148.462 | #NAME?
5-Bed Ward 3 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5217 | #NAME?
5-Bed Ward 4 | 136.47 | 10.0078 | 34.5 | 22.5 | 0.018137 | #NAME? | 147.7151 | #NAME?
5-Bed Ward 4 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5217 | #NAME?
Isolation Room 1 | 54.6952 | 4.011 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.2021 | #NAME?
Isolation Room 1 CR | 10.4924 | 0.73884 | 34.5 | 24 | 0.018137 | #NAME? | 9.5421 | #NAME?
Private Room 1 | 55.6824 | 4.0834 | 34.5 | 22.5 | 0.018137 | #NAME? | 60.2706 | #NAME?
Private Room 1 CR | 10.462 | 0.7367 | 34.5 | 24 | 0.018137 | #NAME? | 9.5145 | #NAME?
Private Room 2 | 55.5016 | 4.0701 | 34.5 | 22.5 | 0.018137 | #NAME? | 60.0749 | #NAME?
Private Room 2 CR | 10.4788 | 0.73788 | 34.5 | 24 | 0.018137 | #NAME? | 9.5297 | #NAME?
Chief Nurse | 122.848 | 9.0089 | 34.5 | 22.5 | 0.018137 | #NAME? | 132.9707 | #NAME?
Chief Nurse CR | 10.5496 | 0.74287 | 34.5 | 24 | 0.018137 | #NAME? | 9.5941 | #NAME?
Treatment Room | 71.7652 | 5.2628 | 34.5 | 22.5 | 0.018137 | #NAME? | 77.6787 | #NAME?
Hallway | 91.316 | 5.7199 | 34.5 | 28 | 0.018137 | #NAME? | 45.7309 | #NAME?
Nurse Station CR | 9.6484 | 0.67941 | 34.5 | 24 | 0.018137 | #NAME? | 8.7746 | #NAME?
Dirty Utility | 19.1476 | 1.3483 | 34.5 | 24 | 0.018137 | #NAME? | 17.4134 | #NAME?
Clean Linen | 9.8324 | 0.69236 | 34.5 | 24 | 0.018137 | #NAME? | 8.9419 | #NAME?
Private Room 3 | 55.494 | 4.0696 | 34.5 | 22.5 | 0.018137 | #NAME? | 60.0667 | #NAME?
Private Room 3 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5217 | #NAME?
Private Room 4 | 55.5712 | 4.0752 | 34.5 | 22.5 | 0.018137 | #NAME? | 60.1503 | #NAME?
Private Room 4 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5217 | #NAME?
Isolation Room 2 | 54.8264 | 4.0206 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.3441 | #NAME?
Isolation Room 2 CR | 10.4852 | 0.73833 | 34.5 | 24 | 0.018137 | #NAME? | 9.5356 | #NAME?
Reception | 44.2088 | 3.242 | 34.5 | 22.5 | 0.018137 | #NAME? | 47.8516 | #NAME?
Private Room 5 | 54.7252 | 4.0132 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.2346 | #NAME?
Private Room 5 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6036 | #NAME?
Chief of Hospital | 74.9276 | 5.4947 | 34.5 | 22.5 | 0.018137 | #NAME? | 81.1016 | #NAME?
Chief of Hospital CR | 27.7184 | 1.9518 | 34.5 | 24 | 0.018137 | #NAME? | 25.208 | #NAME?
3-Bed Ward 1 | 101.488 | 7.4425 | 34.5 | 22.5 | 0.018137 | #NAME? | 109.8506 | #NAME?
3-Bed Ward 1 CR | 10.4348 | 0.73478 | 34.5 | 24 | 0.018137 | #NAME? | 9.4897 | #NAME?
Elevator | 26.4604 | 1.9404 | 34.5 | 22.5 | 0.018137 | #NAME? | 28.6407 | #NAME?
3-Bed Ward 2 | 101.92 | 7.4741 | 34.5 | 22.5 | 0.018137 | #NAME? | 110.3182 | #NAME?
3-Bed Ward 2 CR | 10.4348 | 0.73478 | 34.5 | 24 | 0.018137 | #NAME? | 9.4897 | #NAME?
Private Room 6 | 55.0048 | 4.0337 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.5372 | #NAME?
Private Room 6 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6036 | #NAME?
Conference Room | 153.8148 | 11.2798 | 34.5 | 22.5 | 0.018137 | #NAME? | 166.4891 | #NAME?
3-Bed Ward 3 | 101.488 | 7.4425 | 34.5 | 22.5 | 0.018137 | #NAME? | 109.8506 | #NAME?
3-Bed Ward 3 CR | 10.4348 | 0.73478 | 34.5 | 24 | 0.018137 | #NAME? | 9.4897 | #NAME?
3-Bed Ward 4 | 101.92 | 7.4741 | 34.5 | 22.5 | 0.018137 | #NAME? | 110.3182 | #NAME?
3-Bed Ward 4 CR | 10.4348 | 0.73478 | 34.5 | 24 | 0.018137 | #NAME? | 9.4897 | #NAME?
Private Room 7 | 55.0048 | 4.0337 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.5372 | #NAME?
Private Room 7 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6036 | #NAME?
Private Room 8 | 55.0048 | 4.0337 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.5372 | #NAME?
Private Room 8 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6036 | #NAME?
Chief of Clinics | 85.4464 | 6.2661 | 34.5 | 22.5 | 0.018137 | #NAME? | 92.4872 | #NAME?
Chief of Clinics CR | 6.6584 | 0.46886 | 34.5 | 24 | 0.018137 | #NAME? | 6.0554 | #NAME?
CSSR | 125.7552 | 9.222 | 34.5 | 22.5 | 0.018137 | #NAME? | 136.1174 | #NAME? | 13.6184
Delivery Room | 139.9448 | 10.3987 | 34.5 | 22 | 0.018137 | #NAME? | 159.8796 | #NAME?
Sub-Ster Room 1 | 21.6444 | 1.5241 | 34.5 | 24 | 0.018137 | #NAME? | 19.6841 | #NAME?
Labor Room | 102.9944 | 7.5529 | 34.5 | 22.5 | 0.018137 | #NAME? | 111.4811 | #NAME?
Labor Room CR | 15.452 | 1.0881 | 34.5 | 24 | 0.018137 | #NAME? | 14.0525 | #NAME?
Pathologic Nursery | 67.1976 | 4.9278 | 34.5 | 22.5 | 0.018137 | #NAME? | 72.7347 | #NAME?
Pre-mature nursery | 67.1996 | 4.928 | 34.5 | 22.5 | 0.018137 | #NAME? | 72.7368 | #NAME?
Breastfeeding room | 40.9032 | 2.9996 | 34.5 | 22.5 | 0.018137 | #NAME? | 44.2736 | #NAME?
Pre-operation area | 76.0028 | 5.6474 | 34.5 | 22 | 0.018137 | #NAME? | 86.8292 | #NAME?
Autoclave area | 59.95 | 4.3963 | 34.5 | 22.5 | 0.018137 | #NAME? | 64.8899 | #NAME?
Autoclave area CR | 6.72 | 0.4732 | 34.5 | 24 | 0.018137 | #NAME? | 6.1114 | #NAME?
Sterile supply room | 86.4024 | 6.0842 | 34.5 | 24 | 0.018137 | #NAME? | 78.577 | #NAME?
Work Area 1 | 94.4012 | 6.9228 | 34.5 | 22.5 | 0.018137 | #NAME? | 102.1799 | #NAME?
Major Operating Room | 140.17 | 10.4154 | 34.5 | 22 | 0.018137 | #NAME? | 160.1369 | #NAME?
Sub-Ster Room 2 | 22.7648 | 1.603 | 34.5 | 24 | 0.018137 | #NAME? | 20.703 | #NAME?
Jan.Clo. | 16.5352 | 1.1644 | 34.5 | 24 | 0.018137 | #NAME? | 15.0376 | #NAME?
Clean up room | 51.64 | 3.6363 | 34.5 | 24 | 0.018137 | #NAME? | 46.963 | #NAME?
Sterile Instrument Supply Storage Area | 29.9136 | 2.1064 | 34.5 | 24 | 0.018137 | #NAME? | 27.2044 | #NAME?
Anesthesia Office & Storage | 70.0828 | 4.935 | 34.5 | 24 | 0.018137 | #NAME? | 63.7355 | #NAME?
DR-1 | 11.2 | 0.78867 | 34.5 | 24 | 0.018137 | #NAME? | 10.1856 | #NAME?
DR-2 | 11.2 | 0.78867 | 34.5 | 24 | 0.018137 | #NAME? | 10.1856 | #NAME?
DR-3 | 11.2 | 0.78867 | 34.5 | 24 | 0.018137 | #NAME? | 10.1856 | #NAME?
Lounge Area | 165.2084 | 12.1153 | 34.5 | 22.5 | 0.018137 | #NAME? | 178.8216 | #NAME?
Recovery Room | 187.8968 | 13.7791 | 34.5 | 22.5 | 0.018137 | #NAME? | 203.3795 | #NAME?
Recovery Room CR | 8.3604 | 0.58871 | 34.5 | 24 | 0.018137 | #NAME? | 7.6032 | #NAME?
[5 empty] | Total: |  | 5646.477 | #NAME?
[5 empty] | Overall Total Load |  | #NAME?
THIRD FLOOR
Space | Volume | L/s | To | Ti | Wo | Wi | Qs | Ql
5-Bed Ward 1 | 137.1076 | 10.0546 | 34.5 | 22.5 | 0.018137 | #NAME? | 148.6466 | #NAME?
5-Bed Ward 1 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5372 | #NAME?
5-Bed Ward 2 | 137.04 | 10.0496 | 34.5 | 22.5 | 0.018137 | #NAME? | 148.5733 | #NAME?
5-Bed Ward 2 CR | 10.47 | 0.7678 | 34.5 | 22.5 | 0.018137 | #NAME? | 11.3512 | #NAME?
Waiting Area 1 | 149.6348 | 9.373 | 34.5 | 28 | 0.018137 | #NAME? | 75.0586 | #NAME?
Waiting Area 2 | 149.6348 | 9.373 | 34.5 | 28 | 0.018137 | #NAME? | 75.0586 | #NAME?
5-Bed Ward 3 | 137.04 | 10.0496 | 34.5 | 22.5 | 0.018137 | #NAME? | 148.5733 | #NAME?
5-Bed Ward 3 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5372 | #NAME?
5-Bed Ward 4 | 137.04 | 10.0496 | 34.5 | 22.5 | 0.018137 | #NAME? | 148.5733 | #NAME?
5-Bed Ward 4 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5372 | #NAME?
Isolation Room 1 | 40.5572 | 2.9742 | 34.5 | 22.5 | 0.018137 | #NAME? | 43.9705 | #NAME?
Isolation Room 1 CR | 10.4888 | 0.73859 | 34.5 | 24 | 0.018137 | #NAME? | 9.5544 | #NAME?
Private Room 1 | 55.6888 | 4.0838 | 34.5 | 22.5 | 0.018137 | #NAME? | 60.3756 | #NAME?
Private Room 1 CR | 10.462 | 0.7367 | 34.5 | 24 | 0.018137 | #NAME? | 9.5299 | #NAME?
Private Room 2 | 55.4952 | 4.0696 | 34.5 | 22.5 | 0.018137 | #NAME? | 60.1657 | #NAME?
Private Room 2 CR | 10.4744 | 0.73757 | 34.5 | 24 | 0.018137 | #NAME? | 9.5412 | #NAME?
Chief Nurse | 122.848 | 9.0089 | 34.5 | 22.5 | 0.018137 | #NAME? | 133.1869 | #NAME?
Chief Nurse CR | 10.5496 | 0.74287 | 34.5 | 24 | 0.018137 | #NAME? | 9.6097 | #NAME?
Treatment Room | 71.7652 | 5.2628 | 34.5 | 22.5 | 0.018137 | #NAME? | 77.805 | #NAME?
Hallway | 91.316 | 5.7199 | 34.5 | 28 | 0.018137 | #NAME? | 45.8052 | #NAME?
Nurse Station CR | 9.66 | 0.68022 | 34.5 | 24 | 0.018137 | #NAME? | 8.7994 | #NAME?
Dirty Utility | 19.1476 | 1.3483 | 34.5 | 24 | 0.018137 | #NAME? | 17.4417 | #NAME?
Clean Linen | 9.8324 | 0.69236 | 34.5 | 24 | 0.018137 | #NAME? | 8.9564 | #NAME?
Private Room 3 | 55.494 | 4.0696 | 34.5 | 22.5 | 0.018137 | #NAME? | 60.1644 | #NAME?
Private Room 3 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5372 | #NAME?
Private Room 4 | 55.5712 | 4.0752 | 34.5 | 22.5 | 0.018137 | #NAME? | 60.2481 | #NAME?
Private Room 4 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5372 | #NAME?
Isolation Room 2 | 40.6864 | 2.9837 | 34.5 | 22.5 | 0.018137 | #NAME? | 44.1106 | #NAME?
Isolation Room 2 CR | 10.4852 | 0.73833 | 34.5 | 24 | 0.018137 | #NAME? | 9.5511 | #NAME?
Private Room 5 | 63.4476 | 4.6528 | 34.5 | 22.5 | 0.018137 | #NAME? | 68.7874 | #NAME?
Private Room 5 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Private Room 6 | 63.4476 | 4.6528 | 34.5 | 22.5 | 0.018137 | #NAME? | 68.7874 | #NAME?
Private Room 6 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
3-Bed Ward 1 | 99.132 | 7.2697 | 34.5 | 22.5 | 0.018137 | #NAME? | 107.4749 | #NAME?
3-Bed Ward 1 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
3-Bed Ward 2 | 99.5636 | 7.3013 | 34.5 | 22.5 | 0.018137 | #NAME? | 107.9429 | #NAME?
3-Bed Ward 2 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Private Room 7 | 54.7252 | 4.0132 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.3309 | #NAME?
Private Room 7 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Private Room 8 | 55.0048 | 4.0337 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.634 | #NAME?
Private Room 8 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Private Room 9 | 64.0448 | 4.6966 | 34.5 | 22.5 | 0.018137 | #NAME? | 69.4348 | #NAME?
Private Room 9 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Private Room 10 | 64.0448 | 4.6966 | 34.5 | 22.5 | 0.018137 | #NAME? | 69.4348 | #NAME?
Private Room 10 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Elevator | 35.8604 | 2.6298 | 34.5 | 22.5 | 0.018137 | #NAME? | 38.8784 | #NAME?
Private Room 11 | 55.0048 | 4.0337 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.634 | #NAME?
Private Room 11 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Private Room 12 | 55.0048 | 4.0337 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.634 | #NAME?
Private Room 12 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Waiting Area | 93.9316 | 5.8838 | 34.5 | 28 | 0.018137 | #NAME? | 47.1172 | #NAME?
Private Room 13 | 43.0288 | 3.1554 | 34.5 | 22.5 | 0.018137 | #NAME? | 46.6501 | #NAME?
Private Room 13 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Private Room 14 | 45.26 | 3.3191 | 34.5 | 22.5 | 0.018137 | #NAME? | 49.0691 | #NAME?
Private Room 14 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Solarium 1 | 53.2332 | 3.9038 | 34.5 | 22.5 | 0.018137 | #NAME? | 57.7133 | #NAME?
Stretcher's Wheelchair Nook 1 | 44.3488 | 2.778 | 34.5 | 28 | 0.018137 | #NAME? | 22.2459 | #NAME?
Stretcher's Wheelchair Nook 2 | 33.1 | 2.0733 | 34.5 | 28 | 0.018137 | #NAME? | 16.6034 | #NAME?
Solarium 2 | 53.87 | 3.9505 | 34.5 | 22.5 | 0.018137 | #NAME? | 58.4037 | #NAME?
Water Tank 1 and 2 | 735.7752 | 51.8108 | 34.5 | 24 | 0.018137 | #NAME? | 670.225 | #NAME?
Chapel | 235.4404 | 14.7477 | 34.5 | 28 | 0.018137 | #NAME? | 118.0998 | #NAME?
Male Toilet | 69.7808 | 4.9137 | 34.5 | 24 | 0.018137 | #NAME? | 63.564 | #NAME?
Female Toilet | 69.9224 | 4.9237 | 34.5 | 24 | 0.018137 | #NAME? | 63.693 | #NAME?
Waiting Area | 174.3656 | 12.7868 | 34.5 | 22.5 | 0.018137 | #NAME? | 189.0402 | #NAME?
Admitting | 43.6024 | 3.1975 | 34.5 | 22.5 | 0.018137 | #NAME? | 47.272 | #NAME? | 43.5914
Billing | 43.1324 | 3.163 | 34.5 | 22.5 | 0.018137 | #NAME? | 46.7624 | #NAME?
Cashier | 37.6652 | 2.7621 | 34.5 | 22.5 | 0.018137 | #NAME? | 40.8351 | #NAME?
Personel's dining | 107.9832 | 7.6038 | 34.5 | 24 | 0.018137 | #NAME? | 98.363 | #NAME?
Personel's dining CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
HALLWAY | 2512.0732 | 157.3535 | 34.5 | 28 | 0.018137 | #NAME? | 1260.0866 | #NAME?
Private Room 16 | 42.8 | 3.1387 | 34.5 | 22.5 | 0.018137 | #NAME? | 46.402 | #NAME?
Private Room 16 CR | 10.4 | 0.73233 | 34.5 | 24 | 0.018137 | #NAME? | 9.4735 | #NAME?
Private Room 15 | 44.8 | 3.2853 | 34.5 | 22.5 | 0.018137 | #NAME? | 48.5704 | #NAME?
Private Room 15 CR | 10.8 | 0.7605 | 34.5 | 24 | 0.018137 | #NAME? | 9.8378 | #NAME?
[5 empty] | Total |  | 5262.1037 | #NAME?
[5 empty] | Total Load |  | #NAME?

## MISCELLANEOUS LOAD
MISCELLANEOUS LOAD
FIRST FLOOR
SPACE | Equipment | WATTAGE | Cs | Cl | CLF | Qs (W) | Ql (W) |  |  | Summary of Data
Maintenance office | CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 70.8 | 0.33 | 0.16 | 0.96 | 22.4294 | 11.328 |  |  |  | QS | QL | Q
Minor operating room | SMOKE DETECTOR, 0.4W CARDIOPULMONARY BYPASS MACHINE, 150 W SURGICAL LGHTS, 25W AUTOCLAVE, 2000W ELECTROSURGERY, 109 W | 2284.4 | 0.33 | 0.16 | 0.96 | 723.6979 | 365.504 |  |  | FIRST FLOOR | 5447.2493 | 2751.136 | 8198.3853
Examination/Treament Area | CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 70.8 | 0.33 | 0.16 | 0.96 | 22.4294 | 11.328 |  |  | SECOND FLOOR | 3484.8253 | 1760.0128 | 5244.8381
Supply Room | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128 |  |  | THIRD FLOOR | 2187.5737 | 1104.8352 | 3292.4089
Pharmacy | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128 |  |  | TOTAL | 11119.6483 | 5615.984 | 16735.6323
Medical records office | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Philhealth | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Doctors on duty | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Emergency room | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128 | 117.7229 | 59.456
Patho. office | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Radiologist office | TV, 125W TELEPHONE, 5W SMOKE DETECTOR, 1.6W CEILING ORBITAL FAN, 70W | 201.6 | 0.33 | 0.16 | 0.96 | 63.8669 | 32.256
X-ray Room | X-RAY MACHINE, 1500W SMOKE DETECTOR, 0.8W | 1500.8 | 0.33 | 0.16 | 0.96 | 475.4534 | 240.128
OPD Clinic Dental 1 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic Dental 2 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic surgery 1 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic surgery 1 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic Pedia 1 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic Pedia 2 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic Medical 1 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic Medical 2 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD info and admitting 1 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD ob-gyne | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Cashier | TV, 125W TELEPHONE, 5W CASH REGISTER, 100W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 525.8 | 0.33 | 0.16 | 0.96 | 166.5734 | 84.128
Billing | TV, 125W TELEPHONE, 5W CASH REGISTER, 100W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 525.8 | 0.33 | 0.16 | 0.96 | 166.5734 | 84.128
Admitting | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Administrative Office | TELEPHONE, 5W TV, 125W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 425.8 | 0.33 | 0.16 | 0.96 | 134.8934 | 68.128
Admin Office | TELEPHONE, 5W TV, 125W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 425.8 | 0.33 | 0.16 | 0.96 | 134.8934 | 68.128
Social Welfare | TELEPHONE, 5W TV, 125W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 425.8 | 0.33 | 0.16 | 0.96 | 134.8934 | 68.128
OPD info and admitting 2 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Ultrasound | TV, 150W TELEPHONE, 5W ULTRASOUND MACHINE, 95W SMOKE DETECTOR, 0.4W | 250.4 | 0.33 | 0.16 | 0.96 | 79.3267 | 40.064
OPD ob-gyne | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Canteen | TV, 150W TELEPHONE, 5W SMOKE DETECTOR, 1.2W CEILING ORBITAL FAN, 70W EXHAUST FAN, 40W | 266.2 | 0.33 | 0.16 | 0.96 | 84.3322 | 42.592
Dietitians office | TV, 150W TELEPHONE, 5W SMOKE DETECTOR, 0.4W | 155.4 | 0.33 | 0.16 | 0.96 | 49.2307 | 24.864
dry storage | SMOKE DETECTOR, 0.4W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
cold storage | SMOKE DETECTOR, 0.4W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Supply recieving area | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Cadaver Holding Room | SMOKE DETECTOR, 0.4W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Nurse Station | TV, 125 W TELEPHONE, 5 W COMPUTER, 225 W | 355 | 0.33 | 0.16 | 0.96 | 112.464 | 56.8
Hallway | SMOKE DETECTOR, 0.8W SPEAKER, 4W FIRE ALARM, 1 W CCTV(14), 56W | 61.8 | 0.33 | 0.16 | 0.96 | 19.5782 | 9.888
Cooking Area | OVEN, 1200 W REFRIGERATOR, 780W WATER DISPENSER, 600W | 2580 | 0.33 | 0.16 | 0.96 | 817.344 | 412.8 | 1055.0707 | 532.864
Staff Dining | SMOKE DETECTOR, 0.4W FRIDGE, 150W WATER DISPENSER, 600W | 750.4 | 0.33 | 0.16 | 0.96 | 237.7267 | 120.064
|  |  |  | Total |  | 5447.2493 | 2751.136
|  |  |  | Total Load |  | 8198.3853
SECOND FLOOR
SPACE | Equipment | Wattage | CS | Cl | CLF | Qs (W) | Ql (W)
5- Bed Ward 1 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
5- Bed Ward 2 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
5- Bed Ward 3 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
5- Bed Ward 4 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
Isolation Room | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W WALL FAN,25 W | 5.4 | 0.33 | 0.16 | 0.96 | 1.7107 | 0.864
Private Room 1 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 2 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 3 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 4 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 5 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 6 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 7 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 8 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Isolation Room 2 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W | 5.4 | 0.33 | 0.16 | 0.96 | 1.7107 | 0.864
Chief Nurse | SMOKE DETECTOR, 0.4W TELEPHONE, 5W COMPUTER, 225W | 230.4 | 0.33 | 0.16 | 0.96 | 72.9907 | 36.864
Treatment Room | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 70.4 | 0.33 | 0.16 | 0.96 | 22.3027 | 11.264
Nurse Station | TV, 125 W TELEPHONE, 5 W COMPUTER, 225 W | 355 | 0.33 | 0.16 | 0.96 | 112.464 | 56.8
Reception | SMOKE DETECTOR, 0.4W TELEPHONE, 5W | 5.4 | 0.33 | 0.16 | 0.96 | 1.7107 | 0.864
Chief of Hospital | TELEPHONE, 5W TV, 125W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 425.8 | 0.33 | 0.16 | 0.96 | 134.8934 | 68.128
Conference Room | TELEPHONE, 5W TV, 125W COMPUTER, 225W WATER DISPENSER, 600 W SMOKE DETECTOR, 0.8 W | 955.8 | 0.33 | 0.16 | 0.96 | 302.7974 | 152.928
Chief of Clinics | TELEPHONE, 5W TV, 125W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 425.8 | 0.33 | 0.16 | 0.96 | 134.8934 | 68.128
3-Bed Ward 1 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
3-Bed Ward 2 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
3-Bed Ward 3 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
3-Bed Ward 4 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
Delivery Room | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Labor Room | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Pathologic Nursery | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Pre-Mature Nursery | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
BreastFeeding Room | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Pre-operation Area | SMOKE DETECTOR, 0.4W CARDIOPULMONARY BYPASS MACHINE, 150 W SURGICAL LGHTS, 25W AUTOCLAVE, 2000W | 2175.4 | 0.33 | 0.16 | 0.96 | 689.1667 | 348.064
Autoclave Area | AUTOCLAVE, 1400 W SMOKE DETECTOR, 0.4 W | 1400.4 | 0.33 | 0.16 | 0.96 | 443.6467 | 224.064
Sterile Supply Room | TELEPHONE, 15W SMOKE DETECTOR, 0.4 W FRIDGE, 200 W | 215.4 | 0.33 | 0.16 | 0.96 | 68.2387 | 34.464
Recovery Room | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Lounge Area | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Anesthesia Office | SMOKE DETECTOR 0.4 W TELEPHONE, 5 W COMPUTER, 225 W ANESTHESIA SYSTEM, 166 W | 396.4 | 0.33 | 0.16 | 0.96 | 125.5795 | 63.424
Nurse Station | TV, 125 W TELEPHONE, 5 W COMPUTER, 225 W | 355 | 0.33 | 0.16 | 0.96 | 112.464 | 56.8
Major Operating Room | SMOKE DETECTOR, 0.4 W CARDIOPULMONARY BYPASS MACHINE, 150 W SURGICAL LGHTS, 25W VACUUM SUCTION, 302 W AUTOCLAVE, 2000W | 2477.4 | 0.33 | 0.16 | 0.96 | 784.8403 | 396.384
Clean Up Room | SMOKE DETECTOR, 0.4W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Hallway | SMOKE DETECTOR, 0.8W SPEAKER, 4W FIRE ALARM 1 W CCTV (10), 40 W | 45.8 | 0.33 | 0.16 | 0.96 | 14.5094 | 7.328
|  |  |  | Total |  | 3484.8253 | 1760.0128
|  |  |  | Total Load |  | 5244.8381
THIRD FLOOR
SPACE | Equipment | Wattage | Cs | Cl | CLF | Qs (W) | Qw (W)
5- Bed Ward 1 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
5- Bed Ward 2 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
5- Bed Ward 3 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
5- Bed Ward 4 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
Isolation Room | SMOKE DETECTOR, 0.4W TELEPHONE, 5W WALL FAN, 25W TV, 150 W | 175.9 | 0.33 | 0.16 | 0.96 | 55.7251 | 28.144
Private Room 1 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 2 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 3 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 4 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 5 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 6 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 7 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 8 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 9 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 10 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 11 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 12 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 13 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 14 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 15 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 16 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Chief Nurse | SMOKE DETECTOR, 0.4W TELEPHONE, 5W COMPUTER, 225W | 230.4 | 0.33 | 0.16 | 0.96 | 72.9907 | 36.864
Treatment Room | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 70.4 | 0.33 | 0.16 | 0.96 | 22.3027 | 11.264
Nurse Station | TV, 125 W TELEPHONE, 5 W COMPUTER, 225 W | 355 | 0.33 | 0.16 | 0.96 | 112.464 | 56.8
3-Bed Ward 1 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
3-Bed Ward 2 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
Admitting | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128 |  | 428.4403 | 216.384
Billing | TV, 125W TELEPHONE, 5W CASH REGISTER, 100W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 525.8 | 0.33 | 0.16 | 0.96 | 166.5734 | 84.128
Cashier | TV, 125W TELEPHONE, 5W CASH REGISTER, 100W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 525.8 | 0.33 | 0.16 | 0.96 | 166.5734 | 84.128
Personel's Dining | SMOKE DETECTOR, 0.4W Fridge, 150W WATER, DISPENSER 600W Oven 1200W | 1950.4 | 0.33 | 0.16 | 0.96 | 617.8867 | 312.064
Chapel | HEAT DETECTOR, 0.16 W CEILING ORBITAL FAN, 50 W | 50.16 | 0.33 | 0.16 | 0.96 | 15.8907 | 8.0256
Solarium | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
Hallway | SMOKE DETECTOR, 0.8W SPEAKER, 4W FIRE ALARM,1W CCTV (10), 40W | 45.8 | 0.33 | 0.16 | 0.96 | 14.5094 | 7.328
|  |  |  | Total |  | 2187.5737 | 1104.8352
|  |  |  | Total Load |  | 3292.4089

## ROOF LOAD
ROOF LOAD
THIRD FLOOR
TYPE 6, roof without suspended ceiling | [7 empty] | Summary of Data
SPACE | U | Area (m2) | CLTDmax | Ti | Tave | CLTDadj | Q(W) |  | Q
5-Bed Ward 1 | 2.5844 | 34.2769 | 18 | 22.5 | 30.45 | 13.0875 | 1159.3501 | FIRST FLOOR | 0
5-Bed Ward 2 | 2.5844 | 34.26 | 18 | 22.5 | 30.45 | 13.0875 | 1158.7785 | SECOND FLOOR | 0
Waiting Area 1 | 2.5844 | 37.4087 | 18 | 22.5 | 30.45 | 13.0875 | 1265.2772 | THIRD FLOOR | 33330.7627
Waiting Area 2 | 2.5844 | 37.4087 | 18 | 22.5 | 30.45 | 13.0875 | 1265.2772 | TOTAL | 33330.7627
5-Bed Ward 3 | 2.5844 | 34.26 | 18 | 22.5 | 30.45 | 13.0875 | 1158.7785
5-Bed Ward 4 | 2.5844 | 34.26 | 18 | 22.5 | 30.45 | 13.0875 | 1158.7785
Isolation Room 1 | 2.5844 | 10.1393 | 18 | 22.5 | 30.45 | 13.0875 | 342.9423
Private Room 1 | 2.5844 | 13.9222 | 18 | 22.5 | 30.45 | 13.0875 | 470.8916
Private Room 2 | 2.5844 | 13.8738 | 18 | 22.5 | 30.45 | 13.0875 | 469.2546
Chief Nurse | 2.5844 | 30.712 | 18 | 22.5 | 30.45 | 13.0875 | 1038.7742
Treatment Room | 2.5844 | 17.9413 | 18 | 22.5 | 30.45 | 13.0875 | 606.8299
Nurse Station | 2.5844 | 22.829 | 18 | 22.5 | 30.45 | 13.0875 | 772.1469
Dirty Utility | 2.5844 | 4.7869 | 18 | 24 | 30.45 | 11.9625 | 147.9901
Clean Linen | 2.5844 | 2.4581 | 18 | 24 | 30.45 | 11.9625 | 75.9937
Private Room 3 | 2.5844 | 13.8735 | 18 | 22.5 | 30.45 | 13.0875 | 469.2444
Private Room 4 | 2.5844 | 13.8928 | 18 | 22.5 | 30.45 | 13.0875 | 469.8972
Isolation Room 2 | 2.5844 | 10.1716 | 18 | 22.5 | 30.45 | 13.0875 | 344.0348
Private Room 5 | 2.5844 | 15.8619 | 18 | 22.5 | 30.45 | 13.0875 | 536.4982
Private Room 6 | 2.5844 | 15.8619 | 18 | 22.5 | 30.45 | 13.0875 | 536.4982
3-Bed Ward 1 | 2.5844 | 24.783 | 18 | 22.5 | 30.45 | 13.0875 | 838.2372
3-Bed Ward 2 | 2.5844 | 24.8909 | 18 | 22.5 | 30.45 | 13.0875 | 841.8867
Private Room 7 | 2.5844 | 13.6813 | 18 | 22.5 | 30.45 | 13.0875 | 462.7436
Private Room 8 | 2.5844 | 13.7512 | 18 | 22.5 | 30.45 | 13.0875 | 465.1078
Private Room 9 | 2.5844 | 16.0112 | 18 | 22.5 | 30.45 | 13.0875 | 541.548
Private Room 10 | 2.5844 | 16.0112 | 18 | 22.5 | 30.45 | 13.0875 | 541.548
Elevator | 2.5844 | 8.9651 | 18 | 22.5 | 30.45 | 13.0875 | 303.2272
Private Room 11 | 2.5844 | 13.7512 | 18 | 22.5 | 30.45 | 13.0875 | 465.1078
Private Room 12 | 2.5844 | 13.7512 | 18 | 22.5 | 30.45 | 13.0875 | 465.1078
Waiting Area | 2.5844 | 23.4829 | 18 | 22.5 | 30.45 | 13.0875 | 794.2638
Private Room 13 | 2.5844 | 10.7572 | 18 | 22.5 | 30.45 | 13.0875 | 363.8416
Private Room 14 | 2.5844 | 11.315 | 18 | 22.5 | 30.45 | 13.0875 | 382.7081
Solarium 1 | 2.5844 | 13.3083 | 18 | 22.5 | 30.45 | 13.0875 | 450.1276
Stretcher's Wheelchair Nook 1 | 2.5844 | 11.0872 | 18 | 22.5 | 30.45 | 13.0875 | 375.0032
Stretcher's Wheelchair Nook 2 | 2.5844 | 8.275 | 18 | 22.5 | 30.45 | 13.0875 | 279.8859
Solarium 2 | 2.5844 | 13.4675 | 18 | 22.5 | 30.45 | 13.0875 | 455.5122
Water Tank 1 and 2 | 2.5844 | 183.9438 | 18 | 24 | 30.45 | 11.9625 | 5686.7414
Chapel | 2.5844 | 58.8601 | 18 | 22.5 | 30.45 | 13.0875 | 1990.8295
Waiting Area | 2.5844 | 43.5914 | 18 | 22.5 | 30.45 | 13.0875 | 1474.3951
Admitting | 2.5844 | 10.9006 | 18 | 22.5 | 30.45 | 13.0875 | 368.6918
Billing | 2.5844 | 10.7831 | 18 | 22.5 | 30.45 | 13.0875 | 364.7176
Cashier | 2.5844 | 9.4163 | 18 | 22.5 | 30.45 | 13.0875 | 318.4882
Personel's dining | 2.5844 | 26.9958 | 18 | 22.5 | 30.45 | 13.0875 | 913.0809
Private Room 15 | 2.5844 | 11.2 | 18 | 22.5 | 30.45 | 13.0875 | 378.8184
Private Room 16 | 2.5844 | 10.7 | 18 | 22.5 | 30.45 | 13.0875 | 361.9069
[6 empty] | Total Load | 33330.7627

## PARTITION LOAD
PARTITION LOAD
FIRST FLOOR
Space | Spaces | U | A | Ti | Ti2 | Q |  | Summary of Data
Power House | Hallway | 2.7144 | 22.2 | 22.5 | 28 | 331.4282 | 33.8 |  | Q
| Storage Room | 2.7144 | 11.6 | 22.5 | 24 | 47.2306 |  | FIRST FLOOR | 18554.5391
Work Area | Storage Room | 2.7144 | 10.2 | 22.5 | 24 | 41.5303 | 10.2 | SECOND FLOOR | 19890.5912
Storage Room | Hallway | 2.7144 | 12 | 24 | 28 | 130.2912 | 23.6 | THIRD FLOOR | 17107.3974
| Maintenance Room | 2.7144 | 11.6 | 24 | 22.5 | 47.2306 |  | TOTAL | 55552.5277
Maintenance Room | Hallway | 2.7144 | 26.6 | 22.5 | 28 | 397.1167 | 38.28
| Maintenance Room CR | 2.7144 | 11.68 | 22.5 | 24 | 47.5563
Female Toilet | Hallway | 2.7144 | 36.2 | 24 | 28 | 393.0451 | 36.2
Male Toilet | Hallway | 2.7144 | 36.2 | 24 | 28 | 393.0451 | 36.2
Minor Operating Room | Hallway | 2.7144 | 24.2 | 22 | 28 | 394.1309 | 61.92
| Emergency Room | 2.7144 | 18.8 | 22 | 22.5 | 25.5154
| Examination/Treatment OBS CR | 2.7144 | 7.72 | 22 | 24 | 41.9103
| Equipment and Supply Storage Area | 2.7144 | 11.2 | 22 | 24 | 60.8026
Equipment and Supply Storage | Emergency Room | 2.7144 | 6.4 | 24 | 22.5 | 26.0582 | 6.4
Examination/Treatment OBS | Examination/Treatment OBS CR | 2.7144 | 5.92 | 22.5 | 24 | 24.1039 | 5.92
Emergency Room | Hallway | 2.7144 | 31.2 | 22.5 | 28 | 465.791 | 34.6
| Doctor's on Duty CR | 2.7144 | 3.4 | 22.5 | 24 | 13.8434
Doctor's on Duty | Doctor's on Duty CR | 2.7144 | 10.4 | 22.5 | 24 | 42.3446 | 21
| Hallway | 2.7144 | 10.6 | 22.5 | 28 | 158.2495
Cadaver Holding Room | Hallway | 2.7144 | 10.4 | 22.5 | 28 | 155.2637 | 39.6
| Supply Room | 2.7144 | 24 | 22.5 | 24 | 97.7184
| Work Area Laboratory | 2.7144 | 5.2 | 22.5 | 22 | 7.0574
Supply Room | Hallway | 2.7144 | 41.6 | 24 | 28 | 451.6762 | 63.6
| Work Area Laboratory | 2.7144 | 22 | 24 | 22 | 119.4336
Pharmacy | Bulk Storage | 2.7144 | 15.4 | 22.5 | 24 | 62.7026 | 69.6
| Hallway | 2.7144 | 54.2 | 22.5 | 28 | 809.1626
Bulk Storage | Hallway | 2.7144 | 16.8 | 24 | 28 | 182.4077 | 16.8
Medical Record Office | Hallway | 2.7144 | 45.32 | 22.5 | 28 | 676.5913 | 45.32
Philhealth | Hallway | 2.7144 | 43.8 | 22.5 | 28 | 653.899 | 43.8
Work Area Laboratory | Waiting Area CR | 2.7144 | 9 | 22 | 24 | 48.8592 | 41
| Waiting Area | 2.7144 | 19.8 | 22 | 22.5 | 26.8726
| Hallway | 2.7144 | 12.2 | 22 | 28 | 198.6941
Film File Storage | Waiting Area | 2.7144 | 5.8 | 24 | 22.5 | 23.6153 | 25.24
| Dark Room | 2.7144 | 14.6 | 24 | 22.5 | 59.4454
| Radiologist Office | 2.7144 | 4.84 | 24 | 22.5 | 19.7065
Waiting Area | Waiting Area CR | 2.7144 | 4.6 | 22.5 | 24 | 18.7294 | 20.6
| Hallway | 2.7144 | 16 | 22.5 | 28 | 238.8672
Dark Room | Waste Disposal Area | 2.7144 | 6 | 22.5 | 24 | 24.4296 | 12.8
| X-Ray Room CR | 2.7144 | 6.8 | 22.5 | 24 | 27.6869
Radiogist Office | Hallway | 2.7144 | 9.4 | 22.5 | 28 | 140.3345 | 9.4
X Ray Room | Waste Disposal Area | 2.7144 | 14.32 | 22.5 | 24 | 58.3053 | 55.44
| Linen Storage | 2.7144 | 19.4 | 22.5 | 24 | 78.989
| Hallway | 2.7144 | 21.72 | 22.5 | 28 | 324.2622
Pressing Area | Washing Area | 2.7144 | 10.2 | 22.5 | 24 | 41.5303 | 29.28
| Linen Storage | 2.7144 | 10.2 | 22.5 | 24 | 41.5303
| Waste Disposal Area | 2.7144 | 8.88 | 22.5 | 24 | 36.1558
Linen Storage | Hallway | 2.7144 | 10.72 | 24 | 28 | 116.3935 | 10.72
Washing Area | Hallway | 2.7144 | 38 | 24 | 28 | 412.5888 | 38
OPD Clinic Dental | Hallway | 2.7144 | 28.4 | 22.5 | 28 | 423.9893 | 28.4
OPD Clinic Dental | Hallway | 2.7144 | 18.4 | 22.5 | 28 | 274.6973 | 18.4
OPD Clinic Pedia | Hallway | 2.7144 | 28.4 | 22.5 | 28 | 423.9893 | 28.4
OPD Clinic Pedia | Hallway | 2.7144 | 8.96 | 22.5 | 28 | 133.7656 | 8.96
Elevator | Hallway | 2.7144 | 19.2 | 22.5 | 28 | 286.6406 | 19.2
OPD Info & Admitting | Hallway | 2.7144 | 16.4 | 22.5 | 28 | 244.8389 | 16.4
OPD Clinic Surgery | Hallway | 2.7144 | 18.64 | 22.5 | 28 | 278.2803 | 18.64
OPD Clinic Medical | Hallway | 2.7144 | 9.2 | 22.5 | 28 | 137.3486 | 9.2
OPD Clinic Surgery | Hallway | 2.7144 | 28.64 | 22.5 | 28 | 427.5723 | 28.64
OPD Clinic Medical | Hallway | 2.7144 | 28.64 | 22.5 | 28 | 427.5723 | 28.64
Cashier | Hallway | 2.7144 | 24 | 22.5 | 28 | 358.3008 | 24
Billing | Hallway | 2.7144 | 11.85 | 22.5 | 28 | 176.911 | 11.85
Admitting | Hallway | 2.7144 | 11.92 | 22.5 | 28 | 177.9561 | 11.92
Administrative Office | Hallway | 2.7144 | 67.2 | 22.5 | 28 | 1003.2422 | 67.2
Admin Office | Hallway | 2.7144 | 16.8 | 22.5 | 28 | 250.8106 | 28.8
| Male Toilet | 2.7144 | 12 | 22.5 | 24 | 48.8592
Social Welfare | Hallway | 2.7144 | 15 | 22.5 | 28 | 223.938 | 27
| Female Toilet | 2.7144 | 12 | 22.5 | 24 | 48.8592
Male Toilet | Hallway | 2.7144 | 33 | 24 | 28 | 358.3008 | 33
Female Toilet | Hallway | 2.7144 | 33 | 24 | 28 | 358.3008 | 33
OPD Info & Admitting | Hallway | 2.7144 | 23.84 | 22.5 | 28 | 355.9121 | 23.84
OPD Records | Hallway | 2.7144 | 25.2 | 22.5 | 28 | 376.2158 | 25.2
Ultrasound | Ultrasound CR | 2.7144 | 11.8 | 22.5 | 24 | 48.0449 | 37.4
| Hallway | 2.7144 | 25.6 | 22.5 | 28 | 382.1875
OPD Clinic OB-Gyne | Hallway | 2.7144 | 44 | 22.5 | 28 | 656.8848 | 55.8
| OPD Clinic OB-Gyne CR | 2.7144 | 11.8 | 22.5 | 24 | 48.0449
Canteen | Hallway | 2.7144 | 24.12 | 24 | 28 | 261.8853 | 48
| Dietary | 2.7144 | 28.6 | 24 | 22.5 | 116.4478
Dietary | Hallway | 2.7144 | 98.44 | 22.5 | 28 | 1469.6304 | 141.44
| Dietitians Office CR | 2.7144 | 12.12 | 22.5 | 24 | 49.3478
| Cold Storage | 2.7144 | 6.12 | 22.5 | 24 | 24.9182
| Dry Storage | 2.7144 | 16.76 | 22.5 | 24 | 68.24
| Garbage Disposal | 2.7144 | 8 | 22.5 | 24 | 32.5728
Supply Receiving Area | Hallway | 2.7144 | 12.92 | 22.5 | 28 | 192.8853 | 24.76
| Cold Storage | 2.7144 | 5.04 | 22.5 | 24 | 20.5209
| Hallway | 2.7144 | 6.8 | 24 | 28 | 73.8317
Dry Storage | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 5.4
Dietitians Office | Dietitians Office CR | 2.7144 | 4.92 | 22.5 | 24 | 20.0323 | 4.92
[5 empty] | Total | 18554.5391
SECOND FLOOR
Space | Spaces | U | A | Ti | Ti2 | Q
5 Bedward | Hallway | 2.7144 | 16.4 | 22.5 | 28 | 244.8389
| 5 Bedward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
5 Bedward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
5 Bedward | Hallway | 2.7144 | 42.4 | 22.5 | 28 | 632.9981
| 5 Bedward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
5 Bedward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
5 Bedward | Hallway | 2.7144 | 42.2 | 22.5 | 28 | 630.0122
| 5 Bedward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
5 Bedward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
5 Bedward | Hallway | 2.7144 | 16.4 | 22.5 | 28 | 244.8389
| 5 Bedward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
5 Bedward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Isolation Room | Hallway | 2.7144 | 4.28 | 22.2 | 28 | 67.3823
| Isolation Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Isolation Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
| Chief of Hospital CR | 2.7144 | 3 | 22.5 | 24 | 12.2148
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 28.4 | 22.5 | 28 | 423.9893
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Chief Nurse | Hallway | 2.7144 | 63.6 | 22.5 | 28 | 949.4971
| Chief Nurse CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Chief Nurse CR | Hallway | 2.7144 | 14.8 | 24 | 28 | 160.6925
Treatment Room | Hallway | 2.7144 | 51.8 | 22.5 | 28 | 773.3326
Dirty Utility | Hallway | 2.7144 | 29.76 | 24 | 28 | 323.1222
Clean Linen | Hallway | 2.7144 | 11.44 | 24 | 28 | 124.2109
Nurse Station CR | Hallway | 2.7144 | 18.72 | 24 | 28 | 203.2543
Private Room | Hallway | 2.7144 | 28.2 | 22.5 | 28 | 421.0034
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Isolation Room | Hallway | 2.7144 | 4.32 | 22.5 | 28 | 64.4941
| Isolation Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Isolation Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Reception | Chief of Hospital CR | 2.7144 | 12 | 22.5 | 24 | 48.8592
| Hallway | 2.7144 | 10.4 | 22.5 | 28 | 155.2637
Chief of Hospital | Hallway | 2.7144 | 10.2 | 22.5 | 28 | 152.2778
| Chief of Hospital CR | 2.7144 | 9.6 | 22.5 | 24 | 39.0874
Conference Room | Hallway | 2.7144 | 22 | 22.5 | 28 | 328.4424
Chief of Clinics | Hallway | 2.7144 | 13.2 | 22.5 | 28 | 197.0654
| Labor Room CR | 2.7144 | 12 | 22.5 | 24 | 48.8592
| Chief of Clinics CR | 2.7144 | 10.4 | 22.5 | 24 | 42.3446
| Delivery Room | 2.7144 | 15.32 | 22.5 | 22 | 20.7923
3 Bed Ward | 3 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
| Hallway | 2.7144 | 51.52 | 22.5 | 28 | 769.1524
3 Bed Ward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
3 Bed Ward | 3 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
| Hallway | 2.7144 | 54.68 | 22.5 | 28 | 816.3287
3 Bed Ward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Elevator | Hallway | 2.7144 | 36.16 | 22.5 | 28 | 539.8399
3 Bed Ward | 3 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
| Hallway | 2.7144 | 47 | 22.5 | 28 | 701.6724
3 Bed Ward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
3 Bed Ward | 3 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
| Hallway | 2.7144 | 56.08 | 22.5 | 28 | 837.2295
3 Bed Ward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Delivery Room | Labor Room CR | 2.7144 | 6.2 | 22 | 24 | 33.6586
| Subster Room | 2.7144 | 6.6 | 22 | 22.5 | 8.9575
| Hallway | 2.7144 | 30.6 | 22 | 28 | 498.3638
Subster Room | Labor Room CR | 2.7144 | 12 | 22.5 | 24 | 48.8592
| Hallway | 2.7144 | 11.2 | 22.5 | 28 | 167.207
Labor Room | Hallway | 2.7144 | 39 | 22.5 | 28 | 582.2388
Pathologic Nursery | Hallway | 2.7144 | 15.6 | 22.5 | 28 | 232.8955
Pre-mature Nursery | Hallway | 2.7144 | 15.92 | 22.5 | 28 | 237.6729
Breastfeeding Room | Hallway | 2.7144 | 9 | 22.5 | 28 | 134.3628
| Pre-Operation Area | 2.7144 | 15.6 | 22.5 | 22 | 21.1723
Work Area | Hallway | 2.7144 | 48 | 22.5 | 28 | 716.6016
| Pre-Operation Area | 2.7144 | 5.4 | 22.5 | 22 | 7.3289
Pre Operation Area | Hallway | 2.7144 | 48.8 | 22 | 28 | 794.7763
CSSR | Hallway | 2.7144 | 52.72 | 22.5 | 28 | 787.0674
| Autoclave Area CR | 2.7144 | 17 | 22.5 | 24 | 69.2172
| Sterile Supply Room | 2.7144 | 24.12 | 22.5 | 24 | 98.207
Sterile Supply Room | Recovery Room | 2.7144 | 12 | 24 | 22.5 | 48.8592
Recovery Room | Hallway | 2.7144 | 24.6 | 22.5 | 28 | 367.2583
| Recovery Room CR | 2.7144 | 11.96 | 22.5 | 24 | 48.6963
Major Operating Room | Hallway | 2.7144 | 36.2 | 22 | 28 | 589.5677
| Subster Room | 2.7144 | 7.2 | 22 | 22.5 | 9.7718
Subster Room | Clean up Room | 2.7144 | 9 | 22.5 | 24 | 36.6444
| Hallway | 2.7144 | 10.72 | 22.5 | 28 | 160.041
Clean up Room | Hallway | 2.7144 | 7 | 24 | 28 | 76.0032
Jan. Clo | Hallway | 2.7144 | 16.8 | 24 | 28 | 182.4077
Sterile Instrument Supply | Hallway | 2.7144 | 9.92 | 24 | 28 | 107.7074
Anesthesia Office & Storage | Hallway | 2.7144 | 22.52 | 24 | 28 | 244.5132
DR 1 | Lounge Area | 2.7144 | 5 | 24 | 22.5 | 20.358
DR 2 | Lounge Area | 2.7144 | 5 | 24 | 22.5 | 20.358
DR 3 | Lounge Area | 2.7144 | 23 | 24 | 22.5 | 93.6468
Lounge Area | Hallway | 2.7144 | 60.6 | 22 | 28 | 986.9558
[5 empty] | Total | 19890.5912
THIRD FLOOR
Space | Spaces | U | A | Ti | Ti2 | Q
5 Bed Ward | Hallway | 2.7144 | 16.4 | 22.5 | 28 | 244.8389
| 5 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
5 Bed Ward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
5 Bed Ward | Hallway | 2.7144 | 42.4 | 22.5 | 28 | 632.9981
| 5 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
5 Bed Ward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
5 Bed Ward | Hallway | 2.7144 | 42.4 | 22.5 | 28 | 632.9981
| 5 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
5 Bed Ward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
5 Bed Ward | Hallway | 2.7144 | 16.4 | 22.5 | 28 | 244.8389
| 5 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
5 Bed Ward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Isolation Room | Hallway | 2.7144 | 4.28 | 22.5 | 28 | 63.897
| Isolation Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Isolation Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 30.8 | 22.5 | 28 | 459.8194
| Private Room CR | 2.7144 | 14.8 | 22.5 | 24 | 60.2597
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Chief Nurse | Hallway | 2.7144 | 62.4 | 22.5 | 28 | 931.5821
| Chief Nurse CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Chief Nurse CR | Hallway | 2.7144 | 14.8 | 24 | 28 | 160.6925
Treatment Room | Hallway | 2.7144 | 60.2 | 22.5 | 28 | 898.7378
Dirty Utility | Hallway | 2.7144 | 29.76 | 24 | 28 | 323.1222
Clean Utility | Hallway | 2.7144 | 11.44 | 24 | 28 | 124.2109
Nurse Station CR | Hallway | 2.7144 | 18.72 | 24 | 28 | 203.2543
Private Room | Hallway | 2.7144 | 28.4 | 22.5 | 28 | 423.9893
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Isolation Room | Hallway | 2.7144 | 4.32 | 22.5 | 28 | 64.4941
| Isolation Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Isolation Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Solarium | Hallway | 2.7144 | 11.8 | 22.5 | 28 | 176.1646
| Water Tank | 2.7144 | 15.2 | 22.5 | 24 | 61.8883
3 Bed Ward | Hallway | 2.7144 | 42.08 | 22.5 | 28 | 628.2207
| 3 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
| Elevator | 2.7144 | 9.4 | 22.5 |  | 574.0956
3 Bed Ward CR | Hallway | 2.7144 | 9.4 | 24 | 28 | 102.0614
| Private Room | 2.7144 | 5.4 | 24 | 22.5 | 21.9866
Private Room | Hallway | 2.7144 | 24.76 | 22.5 | 28 | 369.647
| Private Room CR | 2.7144 | 13.44 | 22.5 | 24 | 54.7223
Private Room CR | Hallway | 2.7144 | 5.44 | 24 | 28 | 59.0653
Private Room | Hallway | 2.7144 | 24.36 | 22.5 | 28 | 363.6753
| Private Room CR | 2.7144 | 13.36 | 22.5 | 24 | 54.3966
Private Room CR | Hallway | 2.7144 | 5.36 | 24 | 28 | 58.1967
Elevator | Hallway | 2.7144 | 27.04 |  | 28 | 2055.1265
| 3 Bed Ward | 2.7144 | 9.4 |  | 22.5 | 574.0956
3 Bed Ward | Hallway | 2.7144 | 42.2 | 22.5 | 28 | 630.0122
| 3 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
3 Bed Ward CR | Hallway | 2.7144 | 9.4 | 24 | 28 | 102.0614
| Private Room | 2.7144 | 5.4 | 24 | 22.5 | 21.9866
Private Room | Hallway | 2.7144 | 24.36 | 22.5 | 28 | 363.6753
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 24.84 | 22.5 | 28 | 370.8413
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631
Solarium | Hallway | 2.7144 | 11.8 | 22.5 | 28 | 176.1646
Waiting Area | Hallway | 2.7144 | 52.8 | 22.5 | 28 | 788.2618
| Personel's Dining | 2.7144 | 8.8 | 22.5 | 24 | 35.8301
Cashier | Personel's Dining | 2.7144 | 12 | 22.5 | 24 | 48.8592
Personel's Dining | Hallway | 2.7144 | 22.4 | 24 | 28 | 243.2102
Female Toilet | Hallway | 2.7144 | 34.92 | 24 | 28 | 379.1474
Male Toilet | Hallway | 2.7144 | 10.72 | 24 | 28 | 116.3935
Water Tank | Hallway | 2.7144 | 16.4 | 24 | 28 | 178.0646
[5 empty] | Total | 17107.3974

## VENTILATION LOAD
VENTILATION LOAD
FIRST FLOOR
SPACE | Occ | L/s | To | Ti | Wo | Wi | Qs (W) | Qw (W) | Area | Column1 | Summary of Data
Maintenance Office | 2 | 16 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 236.544 | 463.4948 | 16.3 | 0.9816 |  | QS | QL | Q
Minor Operating Room | 3 | 45 | 34.5 | 22 | 0.018137 | 0.0082198 | 693 | 1338.7939 | 23.4 | 1.9231 | FIRST FLOOR | 9262.792 | 18303.1547 | 27565.9467
Examination/Treatment Area | 5 | 40 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 591.36 | 1158.737 | 131.3 | 0.30465 | SECOND FLOOR | 20168.764 | #NAME? | #NAME?
Supply Room | 3 | 7.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 110.88 | 217.2632 | 31.3 | 0.23962 | THIRD FLOOR | 13106.016 | #NAME? | #NAME?
Pharmacy | 2 | 16 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 236.544 | 463.4948 | 20.7 | 0.77295 | TOTAL | 42537.572 | #NAME? | #NAME?
Medical Records Office | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 36.6 | 0.13661
PHILHEALTH | 2 | 16 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 236.544 | 463.4948 | 17.1 | 0.93567
Doctor's Duty | 1 | 2.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.96 | 72.4211 | 11.6 | 0.21552
Nurse Station | 14 | 112 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 1655.808 | 3244.4637 |  | #DIV/0!
Work Area Laboratory | 4 | 40 | 34.5 | 22 | 0.018137 | 0.0082198 | 616 | 1190.039 | 32.9 | 1.2158
OPD Clinic Dental | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 14.4 | 0.34722
OPD Clinic Dental | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 14.4 | 0.34722
OPD Clinic Surgery | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 14.4 | 0.34722
OPD Clinic Surgery | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 14.4 | 0.34722
Cashier | 1 | 2.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.96 | 72.4211 | 5.5 | 0.45455
Billing | 1 | 2.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.96 | 72.4211 | 5.5 | 0.45455
Admitting | 1 | 2.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.96 | 72.4211 | 5.6 | 0.44643
Radiologist Office | 1 | 2.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.96 | 72.4211 | 9.1 | 0.27473
Dark Room | 1 | 8 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 118.272 | 231.7474 | 5 | 1.6
Control Booth | 3 | 24 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 354.816 | 695.2422 | 25.3 | 0.94862
OPD Clinic Pedia | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 14.4 | 0.34722
OPD Clinic Pedia | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 14.4 | 0.34722
OPD info. And Admitting | 1 | 2.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.96 | 72.4211 | 10 | 0.25
OPD Clinic Medical | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 14.4 | 0.34722
OPD Clinic Medical | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 14.4 | 0.34722
Admin Office | 1 | 2.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.96 | 72.4211 | 13.6 | 0.18382
Administrative Office | 4 | 10 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 147.84 | 289.6843 | 35.3 | 0.28329
Social Welfare | 1 | 2.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.96 | 72.4211 | 13.6 | 0.18382
OPD Info. And Admitting | 1 | 2.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.96 | 72.4211 | 10.4 | 0.24038
OPD Records | 1 | 2.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.96 | 72.4211 | 11.6 | 0.21552
Ultrasound | 2 | 16 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 236.544 | 463.4948 | 19.1 | 0.8377
Supply Receiving Area | 1 | 2.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.96 | 72.4211 | 5.7 | 0.4386
Dietician's Office | 1 | 2.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.96 | 72.4211 | 9.2 | 0.27174
Dietary | 4 | 10 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 147.84 | 289.6843 |  | #DIV/0!
Staff Dining | 5 | 40 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 591.36 | 1158.737 | 123.1 | 0.32494
OPD clinic Ob-gyne | 3 | 7.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 110.88 | 217.2632 | 27 | 0.27778
Canteen | 20 | 160 | 34.5 | 24 | 0.018137 | 0.0092932 | 2069.76 | 4244.8882 | 181.7 | 0.88057
[6 empty] | Total: | 9262.792 | 18303.1547
[6 empty] | Total Load |  | 27565.9467
SECOND FLOOR
SPACE | Occ. | L/s | To | Ti | Wo | Wi | Qs(W) | Ql(W) | Column1
5-Bed Ward 1 | 5 | 65 | 34.5 | 22.5 | 0.018137 | #NAME? | 960.96 | #NAME? | 13
5-Bed Ward 2 | 5 | 65 | 34.5 | 22.5 | 0.018137 | #NAME? | 960.96 | #NAME? | 13
5-Bed Ward 3 | 5 | 65 | 34.5 | 22.5 | 0.018137 | #NAME? | 960.96 | #NAME? | 13
5-Bed Ward 4 | 5 | 65 | 34.5 | 22.5 | 0.018137 | #NAME? | 960.96 | #NAME? | 13
Isolation Room 1 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 1 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 2 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Chief Nurse | 7 | 17.5 | 34.5 | 22.5 | 0.018137 | #NAME? | 258.72 | #NAME? | 2.5
Treatment Room | 2 | 16 | 34.5 | 22.5 | 0.018137 | #NAME? | 236.544 | #NAME? | 8
Nurse Station | 5 | 40 | 34.5 | 22.5 | 0.018137 | #NAME? | 591.36 | #NAME? | 8
Dirty Utility | 1 | 2.5 | 34.5 | 24 | 0.018137 | #NAME? | 32.34 | #NAME? | 2.5
Clean Linen | 1 | 2.5 | 34.5 | 24 | 0.018137 | #NAME? | 32.34 | #NAME? | 2.5
Private Room 3 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 4 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Isolation Room 2 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Reception | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 5 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Chief of Hospital | 3 | 7.5 | 34.5 | 22.5 | 0.018137 | #NAME? | 110.88 | #NAME? | 2.5
3-Bed Ward 1 | 3 | 39 | 34.5 | 22.5 | 0.018137 | #NAME? | 576.576 | #NAME? | 13
3-Bed Ward 2 | 3 | 39 | 34.5 | 22.5 | 0.018137 | #NAME? | 576.576 | #NAME? | 13
Private Room 6 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Conference Room | 8 | 104 | 34.5 | 22.5 | 0.018137 | #NAME? | 1537.536 | #NAME? | 13
3-Bed Ward 3 | 3 | 39 | 34.5 | 22.5 | 0.018137 | #NAME? | 576.576 | #NAME? | 13
3-Bed Ward 4 | 3 | 39 | 34.5 | 22.5 | 0.018137 | #NAME? | 576.576 | #NAME? | 13
Private Room 7 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 8 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Chief of Clinics | 5 | 12.5 | 34.5 | 22.5 | 0.018137 | #NAME? | 184.8 | #NAME? | 2.5
Delivery Room | 8 | 64 | 34.5 | 22 | 0.018137 | #NAME? | 985.6 | #NAME? | 8
Sub-Ster Room 1 | 1 | 2.5 | 34.5 | 24 | 0.018137 | #NAME? | 32.34 | #NAME? | 2.5
Labor Room | 6 | 48 | 34.5 | 22.5 | 0.018137 | #NAME? | 709.632 | #NAME? | 8
Pathologic Nursery | 4 | 10 | 34.5 | 22.5 | 0.018137 | #NAME? | 147.84 | #NAME? | 2.5
Pre-mature nursery | 4 | 10 | 34.5 | 22.5 | 0.018137 | #NAME? | 147.84 | #NAME? | 2.5
Breastfeeding room | 2 | 5 | 34.5 | 22.5 | 0.018137 | #NAME? | 73.92 | #NAME? | 2.5
Pre-operation area | 4 | 60 | 34.5 | 22 | 0.018137 | #NAME? | 924 | #NAME? | 15
Autoclave area | 3 | 24 | 34.5 | 22.5 | 0.018137 | #NAME? | 354.816 | #NAME? | 8
Sterile Supply room | 5 | 12.5 | 34.5 | 24 | 0.018137 | #NAME? | 161.7 | #NAME? | 2.5
Major Operating Room | 8 | 120 | 34.5 | 22 | 0.018137 | #NAME? | 1848 | #NAME? | 15
Sub-Ster Room 2 | 1 | 2.5 | 34.5 | 24 | 0.018137 | #NAME? | 32.34 | #NAME? | 2.5
Jan.Clo. | 1 | 2.5 | 34.5 | 24 | 0.018137 | #NAME? | 32.34 | #NAME? | 2.5
Clean up room | 3 | 7.5 | 34.5 | 24 | 0.018137 | #NAME? | 97.02 | #NAME? | 2.5
Sterile Instrument Supply Storage Area | 2 | 5 | 34.5 | 24 | 0.018137 | #NAME? | 64.68 | #NAME? | 2.5
Anesthesia Office & Storage | 4 | 10 | 34.5 | 24 | 0.018137 | #NAME? | 129.36 | #NAME? | 2.5
Lounge Area | 3 | 24 | 34.5 | 22.5 | 0.018137 | #NAME? | 354.816 | #NAME? | 8
Recovery Room | 6 | 48 | 34.5 | 22.5 | 0.018137 | #NAME? | 709.632 | #NAME? | 8
[6 empty] | Total | 20168.764 | #NAME?
[6 empty] | Total Load |  | #NAME?
THIRD FLOOR
Space | Occ. | L/s | To | Ti | Wo | Wi | Qs(W) | Ql(W) | Column1
5-Bed Ward 1 | 5 | 65 | 34.5 | 22.5 | 0.018137 | #NAME? | 960.96 | #NAME? | 13
5-Bed Ward 2 | 5 | 65 | 34.5 | 22.5 | 0.018137 | #NAME? | 960.96 | #NAME? | 13
5-Bed Ward 3 | 5 | 65 | 34.5 | 22.5 | 0.018137 | #NAME? | 960.96 | #NAME? | 13
5-Bed Ward 4 | 5 | 65 | 34.5 | 22.5 | 0.018137 | #NAME? | 960.96 | #NAME? | 13
Isolation Room 1 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 1 | 1 | 13 | 34.5 | 22.5 | 0.018137 | #NAME? | 192.192 | #NAME? | 13
Private Room 2 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Chief Nurse | 7 | 17.5 | 34.5 | 22.5 | 0.018137 | #NAME? | 258.72 | #NAME? | 2.5
Treatment Room | 2 | 16 | 34.5 | 22.5 | 0.018137 | #NAME? | 236.544 | #NAME? | 8
Private Room 3 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 4 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Isolation Room 2 | 1 | 13 | 34.5 | 22.5 | 0.018137 | #NAME? | 192.192 | #NAME? | 13
Private Room 5 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 6 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
3-Bed Ward 1 | 3 | 39 | 34.5 | 22.5 | 0.018137 | #NAME? | 576.576 | #NAME? | 13
3-Bed Ward 2 | 3 | 39 | 34.5 | 22.5 | 0.018137 | #NAME? | 576.576 | #NAME? | 13
Private Room 7 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 8 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 9 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 10 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 11 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 12 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 13 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 14 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Solarium 1 | 2 | 5 | 34.5 | 22.5 | 0.018137 | #NAME? | 73.92 | #NAME? | 2.5
Solarium 2 | 2 | 5 | 34.5 | 22.5 | 0.018137 | #NAME? | 73.92 | #NAME? | 2.5
Admitting | 2 | 5 | 34.5 | 22.5 | 0.018137 | #NAME? | 73.92 | #NAME? | 2.5
Billing | 2 | 5 | 34.5 | 22.5 | 0.018137 | #NAME? | 73.92 | #NAME? | 2.5
Cashier | 2 | 5 | 34.5 | 22.5 | 0.018137 | #NAME? | 73.92 | #NAME? | 2.5
Personel's dining | 6 | 48 | 34.5 | 22.5 | 0.018137 | #NAME? | 709.632 | #NAME? | 8
Private Room 15 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 16 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
[6 empty] | Total | 13106.016 | #NAME?
[6 empty] | Total Load |  | #NAME?

## OCCUPANT LOAD
OCCUPANT LOAD
FIRST FLOOR
SPACE | Occ | Gain/person | Sensible | Latent | CLF | Qs (W) | Ql (W) | Qs/p | Ql/p | Summary of Data
Maintenance Office | 2 | 70 | 0.6 | 0.4 | 0.92 | 77.28 | 25.76 | 38.64 | 12.88 |  | QS | QL | Q
Minor Operating Room | 3 | 150 | 0.5 | 0.5 | 0.92 | 207 | 69 | 69 | 23 | FIRST FLOOR | 6432.18 | 1888.76 | 8320.94
Examination/Treatment Area | 5 | 100 | 0.6 | 0.4 | 0.92 | 276 | 36.8 | 55.2 | 7.36 | SECOND FLOOR | 8765.3 | 6432.5 | 15197.8
Supply Room | 3 | 150 | 0.5 | 0.5 | 0.92 | 207 | 69 | 69 | 23 | THIRD FLOOR | 4519.5 | 2132.1 | 6651.6
Pharmacy | 2 | 150 | 0.5 | 0.5 | 0.92 | 138 | 69 | 69 | 34.5 | TOTAL | 19716.98 | 10453.36 | 30170.34
Medical Records Office | 2 | 150 | 0.55 | 0.45 | 0.92 | 151.8 | 62.1 | 75.9 | 31.05
PHILHEALTH | 2 | 150 | 0.55 | 0.45 | 0.92 | 151.8 | 62.1 | 75.9 | 31.05
Doctor's Duty | 1 | 100 | 0.6 | 0.4 | 0.92 | 55.2 | 36.8 | 55.2 | 36.8
Nurse Station | 14 | 100 | 0.6 | 0.4 | 0.92 | 772.8 | 36.8 | 55.2 | 2.6286
Work Area Laboratory | 4 | 150 | 0.5 | 0.5 | 0.92 | 276 | 69 | 69 | 17.25
OPD Clinic Dental | 2 | 150 | 0.5 | 0.5 | 0.92 | 138 | 69 | 69 | 34.5
OPD Clinic Dental | 2 | 150 | 0.5 | 0.5 | 0.92 | 138 | 69 | 69 | 34.5
OPD Clinic Surgery | 2 | 150 | 0.5 | 0.5 | 0.92 | 138 | 69 | 69 | 34.5
OPD Clinic Surgery | 2 | 150 | 0.5 | 0.5 | 0.92 | 138 | 69 | 69 | 34.5
Cashier | 1 | 150 | 0.55 | 0.45 | 0.92 | 75.9 | 62.1 | 75.9 | 62.1
Billing | 1 | 150 | 0.55 | 0.45 | 0.92 | 75.9 | 62.1 | 75.9 | 62.1
Admitting | 1 | 150 | 0.55 | 0.45 | 0.92 | 75.9 | 62.1 | 75.9 | 62.1
Radiologist Office | 1 | 150 | 0.5 | 0.5 | 0.92 | 69 | 69 | 69 | 69
Dark Room | 1 | 100 | 0.6 | 0.4 | 0.92 | 55.2 | 36.8 | 55.2 | 36.8
Control Booth | 3 | 100 | 0.6 | 0.4 | 0.92 | 165.6 | 36.8 | 55.2 | 12.2667
OPD Clinic Pedia | 2 | 100 | 0.6 | 0.4 | 0.92 | 110.4 | 36.8 | 55.2 | 18.4
OPD Clinic Pedia | 2 | 100 | 0.6 | 0.4 | 0.92 | 110.4 | 36.8 | 55.2 | 18.4
OPD info. And Admitting | 1 | 150 | 0.55 | 0.45 | 0.92 | 75.9 | 62.1 | 75.9 | 62.1
OPD Clinic Medical | 2 | 100 | 0.6 | 0.4 | 0.92 | 110.4 | 36.8 | 55.2 | 18.4
OPD Clinic Medical | 2 | 100 | 0.6 | 0.4 | 0.92 | 110.4 | 36.8 | 55.2 | 18.4
Admin Office | 1 | 150 | 0.55 | 0.45 | 0.92 | 75.9 | 62.1 | 75.9 | 62.1
Administrative Office | 4 | 150 | 0.55 | 0.45 | 0.92 | 303.6 | 62.1 | 75.9 | 15.525
Social Welfare | 1 | 100 | 0.6 | 0.4 | 0.92 | 55.2 | 36.8 | 55.2 | 36.8
OPD Info. And Admitting | 1 | 150 | 0.55 | 0.45 | 0.92 | 75.9 | 62.1 | 75.9 | 62.1
OPD Records |  |  |  |  | 0.92 | 0 | 0 | #DIV/0! | #DIV/0!
Ultrasound | 2 | 100 | 0.6 | 0.4 | 0.92 | 110.4 | 36.8 | 55.2 | 18.4
Supply Receiving Area | 1 | 150 | 0.5 | 0.5 | 0.92 | 69 | 69 | 69 | 69
Dietician's Office | 1 | 150 | 0.55 | 0.45 | 0.92 | 75.9 | 62.1 | 75.9 | 62.1
Dietary | 4 | 100 | 0.6 | 0.4 | 0.92 | 220.8 | 36.8 | 55.2 | 9.2
Staff Dining | 5 | 100 | 0.6 | 0.4 | 0.92 | 276 | 36.8 | 55.2 | 7.36
OPD clinic Ob-gyne | 3 | 100 | 0.6 | 0.4 | 0.92 | 165.6 | 36.8 | 55.2 | 12.2667
Canteen | 20 | 100 | 0.6 | 0.4 | 0.92 | 1104 | 36.8 | 55.2 | 1.84
[5 empty] | Total | 6432.18 | 1888.76
[5 empty] | Total Load |  | 8320.94
SECOND FLOOR
SPACE | Occ | Gain/person | Sensible | Latent | CLF | Qs (W) | Ql (W) | Qs/p | Ql/p
5-Bed Ward 1 | 5 | 70 | 0.75 | 0.25 | 0.92 | 241.5 | 87.5 | 48.3 | 17.5
5-Bed Ward 2 | 5 | 70 | 0.75 | 0.25 | 0.92 | 241.5 | 87.5 | 48.3 | 17.5
5-Bed Ward 3 | 5 | 70 | 0.75 | 0.25 | 0.92 | 241.5 | 87.5 | 48.3 | 17.5
5-Bed Ward 4 | 5 | 70 | 0.75 | 0.25 | 0.92 | 241.5 | 87.5 | 48.3 | 17.5
Isolation Room 1 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35 | 48.3 | 17.5
Private Room 1 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35 | 48.3 | 17.5
Private Room 2 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35 | 48.3 | 17.5
Chief Nurse | 7 | 100 | 0.6 | 0.4 | 0.92 | 386.4 | 280 | 55.2 | 40
Treatment Room | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35 | 48.3 | 17.5
Nurse Station | 5 | 100 | 0.6 | 0.4 | 0.92 | 276 | 200 | 55.2 | 40
Dirty Utility | 1 | 150 | 0.5 | 0.5 | 0.92 | 69 | 75 | 69 | 75
Clean Linen | 1 | 150 | 0.5 | 0.5 | 0.92 | 69 | 75 | 69 | 75
Private Room 3 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35 | 48.3 | 17.5
Private Room 4 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35 | 48.3 | 17.5
Isolation Room 2 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35 | 48.3 | 17.5
Reception | 2 | 100 | 0.6 | 0.4 | 0.92 | 110.4 | 80 | 55.2 | 40
Private Room 5 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35 | 48.3 | 17.5
Chief of Hospital | 3 | 100 | 0.6 | 0.4 | 0.92 | 165.6 | 120 | 55.2 | 40
3-Bed Ward 1 | 3 | 70 | 0.75 | 0.25 | 0.92 | 144.9 | 52.5 | 48.3 | 17.5
3-Bed Ward 2 | 3 | 70 | 0.75 | 0.25 | 0.92 | 144.9 | 52.5 | 48.3 | 17.5
Private Room 6 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35 | 48.3 | 17.5
Conference Room | 8 | 175 | 0.5 | 0.5 | 0.92 | 644 | 700 | 80.5 | 87.5
3-Bed Ward 3 | 3 | 70 | 0.75 | 0.25 | 0.92 | 144.9 | 52.5 | 48.3 | 17.5
3-Bed Ward 4 | 3 | 70 | 0.75 | 0.25 | 0.92 | 144.9 | 52.5 | 48.3 | 17.5
Private Room 7 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35 | 48.3 | 17.5
Private Room 8 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35 | 48.3 | 17.5
Chief of Clinics | 5 | 150 | 0.55 | 0.45 | 0.92 | 379.5 | 337.5 | 75.9 | 67.5
Delivery Room | 8 | 150 | 0.5 | 0.5 | 0.92 | 552 | 600 | 69 | 75
Sub-Ster Room 1 | 1 | 150 | 0.5 | 0.5 | 0.92 | 69 | 75 | 69 | 75
Labor Room | 6 | 150 | 0.5 | 0.5 | 0.92 | 414 | 450 | 69 | 75
Pathologic Nursery | 4 | 70 | 0.75 | 0.25 | 0.92 | 193.2 | 70 | 48.3 | 17.5
Pre-mature nursery | 4 | 70 | 0.75 | 0.25 | 0.92 | 193.2 | 70 | 48.3 | 17.5
Breastfeeding room | 2 | 100 | 0.6 | 0.4 | 0.92 | 110.4 | 80 | 55.2 | 40
Pre-operation area | 4 | 150 | 0.5 | 0.5 | 0.92 | 276 | 300 | 69 | 75
Autoclave area | 3 | 100 | 0.6 | 0.4 | 0.92 | 165.6 | 120 | 55.2 | 40
Sterile Supply room | 5 | 100 | 0.6 | 0.4 | 0.92 | 276 | 200 | 55.2 | 40
Major Operating Room | 8 | 150 | 0.5 | 0.5 | 0.92 | 552 | 600 | 69 | 75
Sub-Ster Room 2 | 1 | 150 | 0.5 | 0.5 | 0.92 | 69 | 75 | 69 | 75
Jan.Clo. | 1 | 150 | 0.5 | 0.5 | 0.92 | 69 | 75 | 69 | 75
Clean up room | 3 | 150 | 0.5 | 0.5 | 0.92 | 207 | 225 | 69 | 75
Sterile Instrument Supply Storage Area | 2 | 100 | 0.6 | 0.4 | 0.92 | 110.4 | 80 | 55.2 | 40
Anesthesia Office & Storage | 4 | 150 | 0.55 | 0.45 | 0.92 | 303.6 | 270 | 75.9 | 67.5
Lounge Area | 3 | 150 | 0.5 | 0.5 | 0.92 | 207 | 225 | 69 | 75
Recovery Room | 6 | 70 | 0.75 | 0.25 | 0.92 | 289.8 | 105 | 48.3 | 17.5
[5 empty] | Total | 8765.3 | 6432.5
[5 empty] | Total Load |  | 15197.8
THIRD FLOOR
SPACE | Occ | Gain/person | Sensible | Latent | CLF | Qs (W) | Ql (W) | Qs/p | Ql/p
5-Bed Ward 1 | 5 | 70 | 0.75 | 0.25 | 0.92 | 241.5 | 80.5 | 48.3 | 16.1
5-Bed Ward 2 | 5 | 70 | 0.75 | 0.25 | 0.92 | 241.5 | 80.5 | 48.3 | 16.1
5-Bed Ward 3 | 5 | 70 | 0.75 | 0.25 | 0.92 | 241.5 | 80.5 | 48.3 | 16.1
5-Bed Ward 4 | 5 | 70 | 0.75 | 0.25 | 0.92 | 241.5 | 80.5 | 48.3 | 16.1
Isolation Room 1 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2 | 48.3 | 16.1
Private Room 1 | 1 | 70 | 0.75 | 0.25 | 0.92 | 48.3 | 16.1 | 48.3 | 16.1
Private Room 2 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2 | 48.3 | 16.1
Chief Nurse | 7 | 150 | 0.55 | 0.45 | 0.92 | 531.3 | 434.7 | 75.9 | 62.1
Treatment Room | 2 | 100 | 0.6 | 0.4 | 0.92 | 110.4 | 73.6 | 55.2 | 36.8
Private Room 3 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2 | 48.3 | 16.1
Private Room 4 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2 | 48.3 | 16.1
Isolation Room 2 | 1 | 70 | 0.75 | 0.25 | 0.92 | 48.3 | 16.1 | 48.3 | 16.1
Private Room 5 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2 | 48.3 | 16.1
Private Room 6 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2 | 48.3 | 16.1
3-Bed Ward 1 | 3 | 70 | 0.75 | 0.25 | 0.92 | 144.9 | 48.3 | 48.3 | 16.1
3-Bed Ward 2 | 3 | 70 | 0.75 | 0.25 | 0.92 | 144.9 | 48.3 | 48.3 | 16.1
Private Room 7 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2 | 48.3 | 16.1
Private Room 8 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2 | 48.3 | 16.1
Private Room 9 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2 | 48.3 | 16.1
Private Room 10 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2 | 48.3 | 16.1
Private Room 11 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2 | 48.3 | 16.1
Private Room 12 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2 | 48.3 | 16.1
Private Room 13 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2 | 48.3 | 16.1
Private Room 14 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2 | 48.3 | 16.1
Solarium 1 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2 | 48.3 | 16.1
Solarium 2 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2 | 48.3 | 16.1
Admitting | 2 | 150 | 0.55 | 0.45 | 0.92 | 151.8 | 124.2 | 75.9 | 62.1
Billing | 2 | 150 | 0.55 | 0.45 | 0.92 | 151.8 | 124.2 | 75.9 | 62.1
Cashier | 2 | 150 | 0.55 | 0.45 | 0.92 | 151.8 | 124.2 | 75.9 | 62.1
Personel's dining | 6 | 100 | 0.6 | 0.4 | 0.92 | 331.2 | 220.8 | 55.2 | 36.8
Private Room 15 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2 | 48.3 | 16.1
Private Room 16 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2 | 48.3 | 16.1
[5 empty] | Total | 4519.5 | 2132.1
[5 empty] | Tota Load |  | 6651.6

## DOOR PARTITION LOAD
LIGHTING LOAD
FIRST FLOOR
Space 1 | Space 2 | U | Area | Ti | To | Qs (W) | Summary of Data
Power House | Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402 |  | Q
Work Area | Storage Room | 1.5625 | 1.8 | 22.5 | 24 | 4.2188 | FIRST FLOOR | 1147.9228
Maintenance Room | Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402 | SECOND FLOOR | 1229.8198
| Maintenance Room CR | 1.6048 | 1.6 | 22.5 | 24 | 3.8515 | THIRD FLOOR | 1068.55
Female Toilet | Hallway | 2.3576 | 1.8 | 24 | 28 | 16.9747 | TOTAL | 3446.2925
Male Toilet | Hallway | 2.3576 | 1.8 | 24 | 28 | 16.9747
Emergency Room | Examination/Treatment Obs Area CR | 2.3576 | 1.8 | 22.5 | 24 | 6.3655
| Hallway | 2.3576 | 3.6 | 22.5 | 28 | 46.6805
| Hallway | 2.3576 | 3.6 | 22.5 | 28 | 46.6805
| Doctor's on Duty CR | 2.3576 | 1.6 | 22.5 | 24 | 5.6582
Minor Operating Room | Emergency Room | 2.3576 | 3.2 | 22 | 22.5 | 3.7722
Equipment and Supply Storage Area | Emergency Room | 2.3576 | 1.8 | 24 | 22.5 | 6.3655
Cadaver Holding Room | Hallway | 2.3576 | 3.6 | 22.5 | 28 | 46.6805
Supply Room | Hallway | 2.3576 | 2 | 22.5 | 28 | 25.9336
Pharmacy | Bulk Storage | 1.5625 | 1.8 | 22.5 | 24 | 4.2188
| Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402
Medical Records Office | Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402
PhilHealth | Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402
Work Area Laboratory | Waiting Area | 2.3576 | 1.8 | 22 | 22.5 | 2.1218
Waiting Area | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Waiting Area CR | 1.6048 | 1.8 | 22.5 | 24 | 4.333
OPD Clinic Dental 1 | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
OPD Clinic Dental 2 | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
OPD Clinic Surgery 1 | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
OPD Clinic Surgery 2 | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
Cashier | Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402
Billing | Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402
Admitting | Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402
Radiologist Office | Film File Storage Room | 2.3576 | 1.8 | 22.5 | 24 | 6.3655
| Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402
XRAY Room | XRAY Room CR | 1.6048 | 1.8 | 22.5 | 24 | 4.333
| Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
OPD Clinic Pedia 1 | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
OPD Clinic Pedia 2 | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
OPD Info & Admitting | Hallway | 2.3576 | 1.6 | 22.5 | 28 | 20.7469
OPD Clinic Medical 1 | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
OPD Clinic Medical 2 | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
Pressing Area | Washing Area | 2.3576 | 1.8 | 22.5 | 24 | 6.3655
| Linen Storage | 2.3576 | 1.8 | 22.5 | 24 | 6.3655
Washing Area | Hallway | 2.3576 | 2 | 22.5 | 28 | 25.9336
| Washing Area CR | 1.6048 | 1.6 | 22.5 | 24 | 3.8515
Administrative Office | Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402
Social Welfare | Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402
Male Toilet | Hallway | 2.3576 | 1.8 | 24 | 28 | 16.9747
Female Toilet | Hallway | 2.3576 | 1.8 | 24 | 28 | 16.9747
OPD Info Admitting | Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402
Ultrasound | Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402
| Ultrasound CR | 1.6048 | 1.8 | 22.5 | 24 | 4.333
Dietary | Dry Storage | 1.5625 | 1.2 | 22.5 | 24 | 2.8125
| Cold Storage | 1.5625 | 1.2 | 22.5 | 24 | 2.8125
| Supply Receive Area | 2.3576 | 1.8 | 22.5 | 24 | 6.3655
| Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402
| Canteen | 1.5625 | 2.4 | 22.5 | 24 | 5.625
Dietician's Office | Dietician's Office CR | 1.6048 | 1.6 | 22.5 | 24 | 3.8515
Canteen | Hallway | 2.3576 | 4 | 24 | 28 | 37.7216
OPD Clinic OB-Gyne | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| OPD Clinic OB-Gyne | 1.6048 | 1.8 | 22.5 | 24 | 4.333
[5 empty] | Total | 1147.9228
SECOND FLOOR
Space 1 | Space 2 | U | Area | Ti | To | Qs (W)
5 Bed Ward | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| 5 Bed Ward CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
5 Bed Ward | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| 5 Bed Ward CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
5 Bed Ward | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| 5 Bed Ward CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
5 Bed Ward | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| 5 Bed Ward CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Isolation Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Isolation Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Chief Nurse | Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402
| Chief Nurse CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Treatment Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
Dirty Utility | Hallway | 2.3576 | 1.2 | 24 | 28 | 11.3165
Clean Linen | Hallway | 2.3576 | 1.2 | 24 | 28 | 11.3165
Nurse Station CR | Hallway | 2.3576 | 1.2 | 24 | 28 | 11.3165
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Isolation Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Isolation Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Reception | Hallway | 2.3576 | 1.6 | 22.5 | 28 | 20.7469
Chief of Hospital | Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402
| Chief of Hospital CR | 1.6048 | 1.2 | 22.5 | 24 | 2.8886
3 Bed Ward | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| 3 Bed Ward CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
3 Bed Ward | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| 3 Bed Ward CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Conference Room | Hallway | 2.3576 | 2 | 22.5 | 28 | 25.9336
3 Bed Ward | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| 3 Bed Ward CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
3 Bed Ward | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| 3 Bed Ward CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Chief of Clinics | Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402
| Chief of Clinics CR | 1.6048 | 1.2 | 22.5 | 24 | 2.8886
CSSR | Hallway | 2.3576 | 2 | 22.5 | 28 | 25.9336
| Sterile Supply Room | 2.3576 | 1.8 | 22.5 | 24 | 6.3655
Delivery Room | Hallway | 2.3576 | 3.2 | 22 | 28 | 45.2659
| Sub Ster Room | 2.3576 | 1.8 | 22 | 24 | 8.4874
Labor Room | Labor Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
| Hallway | 2.3576 | 2 | 22.5 | 28 | 25.9336
| Hallway | 2.3576 | 3.2 | 22.5 | 28 | 41.4938
Breast Feeding Room | Hallway | 2.3576 | 1.6 | 22.5 | 28 | 20.7469
Pre Operation Area | Hallway | 2.3576 | 1.8 | 22 | 28 | 25.4621
Major Operating Room | Hallway | 2.3576 | 3.2 | 22 | 28 | 45.2659
| Sub Ster Room | 2.3576 | 1.8 | 22 | 24 | 8.4874
Jan. Clo | Hallway | 2.3576 | 1.4 | 24 | 28 | 13.2026
Clean Up Room | Hallway | 2.3576 | 2 | 24 | 28 | 18.8608
Sterile Instrument Supply Storage Area | Hallway | 2.3576 | 1.6 | 24 | 28 | 15.0886
Anesthesia Office and Storage | Hallway | 2.3576 | 1.8 | 24 | 28 | 16.9747
Lounge Area | Hallway | 2.3576 | 1.6 | 22.5 | 28 | 20.7469
| Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402
| DR 1 | 1.6048 | 1.2 | 22.5 | 24 | 2.8886
| DR 2 | 1.6048 | 1.2 | 22.5 | 24 | 2.8886
| DR 3 | 1.6048 | 1.2 | 22.5 | 24 | 2.8886
Recovery Room | Hallway | 2.3576 | 3.2 | 22.5 | 28 | 41.4938
| Recovery Room CR | 1.6048 | 1.2 | 22.5 | 24 | 2.8886
[5 empty] | Total | 1229.8198
Space 1 | Space 2 | U | Area | Ti | To | Qs (W)
5 Bed Ward | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| 5 Bed Ward CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
5 Bed Ward | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| 5 Bed Ward CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
5 Bed Ward | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| 5 Bed Ward CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
5 Bed Ward | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| 5 Bed Ward CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Isolation Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Isolation Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Chief Nurse | Hallway | 2.3576 | 1.8 | 22.5 | 28 | 23.3402
| Chief Nurse CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Treatment Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
Dirty Utility | Hallway | 2.3576 | 1.2 | 24 | 28 | 11.3165
Clean Linen | Hallway | 2.3576 | 1.2 | 24 | 28 | 11.3165
Nurse Station CR | Hallway | 2.3576 | 1.2 | 24 | 28 | 11.3165
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Isolation Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Isolation Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
3 Bed Ward | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| 3 Bed Ward CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
3 Bed Ward | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| 3 Bed Ward CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Private Room | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
| Private Room CR | 1.6048 | 1.4 | 22.5 | 24 | 3.3701
Solarium | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
Solarium | Hallway | 2.3576 | 2.4 | 22.5 | 28 | 31.1203
Waiting Area | Hallway | 2.3576 | 3.2 | 22.5 | 28 | 41.4938
| Personel's Dinning | 2.3576 | 3.2 | 22.5 | 24 | 11.3165
Male Toilet | Hallway | 2.3576 | 1.8 | 24 | 28 | 16.9747
Female Toilet | Hallway | 2.3576 | 1.8 | 24 | 28 | 16.9747
[5 empty] | Total | 1068.55

## LIGHTING LOAD
LIGHTING LOAD
FIRST FLOOR
SPACE | W | Fu | Fb | CLF | Qs (W) |  | Summary of Data
1.1 Power House | 486.7018 | 0.75 | 1.2 | 0.94 | 411.7497 |  |  | Q
1.2 Work Area | 125.4656 | 0.75 | 1.2 | 0.94 | 106.1439 |  | FIRST FLOOR | 19883.6097
1.3 Storage Room | 101.6275 | 0.5 | 1.2 | 0.94 | 57.3179 |  | SECOND FLOOR | 16958.0662
1.4 Maintenance Office | 212.0235 | 0.5 | 1.2 | 0.94 | 119.5813 |  | THIRD FLOOR | 22702.4001
1.5 Female toilet | 237.8883 | 0.5 | 1.2 | 0.94 | 134.169 |  | TOTAL | 59544.076
1.6 Male Toilet | 238.5032 | 0.5 | 1.2 | 0.94 | 134.5158
1.7 Minor Operating Room | 304.0518 | 0.5 | 1.2 | 0.94 | 171.4852
1.8 Equipment and supply storage area | 72.93 | 0.75 | 1.2 | 0.94 | 61.6988
1.9 Examination/Treatment Area | 548.5025 | 0.75 | 1.2 | 0.94 | 464.0331
1.10 Cadaver Holding Room | 255.2914 | 0.5 | 1.2 | 0.94 | 143.9843
1.11 Supply Room | 406.7609 | 0.5 | 1.2 | 0.94 | 229.4131
1.12 Bulk Storage | 51.7036 | 0.5 | 1.2 | 0.94 | 29.1608
1.13 Pharmacy | 269.7331 | 0.75 | 1.2 | 0.94 | 228.1942
1.14 Medical Records Office | 233.3656 | 0.75 | 1.2 | 0.94 | 197.4273
1.15 Medical Records | 242.2004 | 0.75 | 1.2 | 0.94 | 204.9015
1.16 PHILHEALTH | 222.7914 | 0.5 | 1.2 | 0.94 | 125.6543
1.17 Doctor's Duty | 150.8806 | 0.5 | 1.2 | 0.94 | 85.0967
1.18 Nurse Station (ER) | 1702.5866 | 0.75 | 1.2 | 0.94 | 1440.3883 | 1904.4214
1.21 Work Area (laboratory) | 427.18 | 0.75 | 1.2 | 0.94 | 361.3943
1.23 Waiting area | 164.8075 | 0.75 | 1.2 | 0.94 | 139.4271
1.24 OPD clinic dental 1 | 186.9543 | 0.5 | 1.2 | 0.94 | 105.4422
1.25 OPD clinic dental 2 | 186.9543 | 0.5 | 1.2 | 0.94 | 105.4422
1.27 OPD clinic surgery 1 | 187.6628 | 0.5 | 1.2 | 0.94 | 105.8418
1.28 OPD clinic surgery 2 | 187.6628 | 0.5 | 1.2 | 0.94 | 105.8418
1.29 Cashier | 71.3375 | 0.75 | 1.2 | 0.94 | 60.3515
1.30 Billing | 71.63 | 0.75 | 1.2 | 0.94 | 60.599
1.31 Admitting | 73.2719 | 0.75 | 1.2 | 0.94 | 61.988
1.32 Film File Storage | 71.7639 | 0.5 | 1.2 | 0.94 | 40.4748
1.33 Radiologist Office | 118.9396 | 0.5 | 1.2 | 0.94 | 67.0819
1.34 Dark Room | 64.3786 | 0.5 | 1.2 | 0.94 | 36.3095
1.35 Control Booth | 328.2994 | 0.5 | 1.2 | 0.94 | 185.1609
1.37 OPD Clinic Pedia 1 | 186.9543 | 0.5 | 1.2 | 0.94 | 105.4422
1.38 OPD Clinic Pedia 2 | 186.9543 | 0.5 | 1.2 | 0.94 | 105.4422
1.39 OPD Records | 135.434 | 0.5 | 1.2 | 0.94 | 76.3848
1.40 OPD info. And admitting | 129.7465 | 0.5 | 1.2 | 0.94 | 73.177
1.41 OPD Clinic Medical 1 | 187.6628 | 0.5 | 1.2 | 0.94 | 105.8418
1.42 OPD Clinic Medical 2 | 187.6628 | 0.5 | 1.2 | 0.94 | 105.8418
1.43 Hospital Main Lobby | 8530.327 | 1 | 1.2 | 0.94 | 9622.2089
1.46 Pressing Area | 109.603 | 0.5 | 1.2 | 0.94 | 61.8161
1.47 Linen Storage | 108.0781 | 0.5 | 1.2 | 0.94 | 60.956
1.49 Linen Office | 109.6875 | 0.5 | 1.2 | 0.94 | 61.8637 | 122.8198
1.50 Admin Office | 176.891 | 0.5 | 1.2 | 0.94 | 99.7665
1.51 Male Toilet | 224.3787 | 0.5 | 1.2 | 0.94 | 126.5496
1.53 Washing Area | 222.6471 | 0.5 | 1.2 | 0.94 | 125.573
1.54 Receiving Sorting Area | 111.4243 | 0.5 | 1.2 | 0.94 | 62.8433 | 188.4163
1.56 Social Welfare | 176.7792 | 0.5 | 1.2 | 0.94 | 99.7035
1.57 Female Toilet | 221.5564 | 0.5 | 1.2 | 0.94 | 124.9578
1.58 OPD Info. And admitting | 135.7421 | 0.5 | 1.2 | 0.94 | 76.5585
1.59 OPD records | 150.6947 | 0.5 | 1.2 | 0.94 | 84.9918
1.60 Ultrasound | 247.9997 | 0.5 | 1.2 | 0.94 | 139.8718
1.61 Cooking Area | 444.7976 | 0.5 | 1.2 | 0.94 | 250.8658 | 1089.3875
1.62 Dry storage | 33.7233 | 0.5 | 1.2 | 0.94 | 19.0199
1.63 Cold Storage | 25.5125 | 0.5 | 1.2 | 0.94 | 14.389
1.64 Supply Receiving Area | 74.3392 | 0.75 | 1.2 | 0.94 | 62.891
1.65 Dietician's Office | 119.925 | 0.5 | 1.2 | 0.94 | 67.6377
1.66 Dietary | 494.4225 | 0.5 | 1.2 | 0.94 | 278.8543
1.67 Staff Dining | 661.5453 | 0.75 | 1.2 | 0.94 | 559.6673
1.68 OPD clinic Ob-gyne | 351.0728 | 0.5 | 1.2 | 0.94 | 198.0051
1.70 Canteen | 2362.0896 | 0.5 | 1.2 | 0.94 | 1332.2185
|  |  |  | Total | 19883.6097
SECOND FLOOR
SPACE | W | Fu | Fb | CLF | Qs (W)
5-Bed Ward 1 | 445.5997 | 0.75 | 1.2 | 0.94 | 376.9773
5-Bed Ward 2 | 445.38 | 0.75 | 1.2 | 0.94 | 376.7915
5-Bed Ward 3 | 445.77 | 0.75 | 1.2 | 0.94 | 377.1214
5-Bed Ward 4 | 443.5275 | 0.75 | 1.2 | 0.94 | 375.2243
Isolation Room 1 | 177.7594 | 0.75 | 1.2 | 0.94 | 150.3845
Private Room 1 | 180.9678 | 0.75 | 1.2 | 0.94 | 153.0988
Private Room 2 | 180.3802 | 0.75 | 1.2 | 0.94 | 152.6016
Chief Nurse | 399.256 | 0.5 | 1.2 | 0.94 | 225.1804
Treatment Room | 233.2369 | 0.75 | 1.2 | 0.94 | 197.3184
Nurse Station | 296.777 | 0.75 | 1.2 | 0.94 | 251.0733
Dirty Utility | 62.2297 | 0.5 | 1.2 | 0.94 | 35.0976
Clean Linen | 31.9553 | 0.5 | 1.2 | 0.94 | 18.0228
Private Room 3 | 180.3555 | 0.75 | 1.2 | 0.94 | 152.5808
Private Room 4 | 180.6064 | 0.75 | 1.2 | 0.94 | 152.793
Isolation Room 2 | 178.1858 | 0.75 | 1.2 | 0.94 | 150.7452
Reception | 143.6786 | 0.5 | 1.2 | 0.94 | 81.0347
Private Room 5 | 177.8569 | 0.75 | 1.2 | 0.94 | 150.4669
Chief of Hospital | 243.5147 | 0.5 | 1.2 | 0.94 | 137.3423
3-Bed Ward 1 | 329.836 | 0.75 | 1.2 | 0.94 | 279.0413
3-Bed Ward 2 | 331.24 | 0.75 | 1.2 | 0.94 | 280.229
Private Room 6 | 178.7656 | 0.75 | 1.2 | 0.94 | 151.2357
Conference Room | 499.8981 | 0.5 | 1.2 | 0.94 | 281.9425
3-Bed Ward 3 | 329.836 | 0.75 | 1.2 | 0.94 | 279.0413
3-Bed Ward 4 | 331.24 | 0.75 | 1.2 | 0.94 | 280.229
Private Room 7 | 178.7656 | 0.75 | 1.2 | 0.94 | 151.2357
Private Room 8 | 178.7656 | 0.75 | 1.2 | 0.94 | 151.2357
Chief of Clinics | 277.7008 | 0.5 | 1.2 | 0.94 | 156.6233
CSSR | 408.7044 | 0.5 | 1.2 | 0.94 | 230.5093 | 340.3976
Delivery Room | 454.8206 | 0.75 | 1.2 | 0.94 | 384.7782
Sub-Ster Room 1 | 70.3443 | 0.75 | 1.2 | 0.94 | 59.5113
Labor Room | 334.7318 | 0.75 | 1.2 | 0.94 | 283.1831
Pathologic Nursery | 218.3922 | 0.75 | 1.2 | 0.94 | 184.7598
Pre-mature nursery | 218.3987 | 0.75 | 1.2 | 0.94 | 184.7653
Breastfeeding room | 132.9354 | 0.5 | 1.2 | 0.94 | 74.9756
Pre-operation area | 247.0091 | 0.5 | 1.2 | 0.94 | 139.3131
Autoclave area | 194.8375 | 0.5 | 1.2 | 0.94 | 109.8884
Sterile supply room | 280.8078 | 0.75 | 1.2 | 0.94 | 237.5634
Work Area 1 | 306.8039 | 0.75 | 1.2 | 0.94 | 259.5561
Major Operating Room | 455.5525 | 0.5 | 1.2 | 0.94 | 256.9316
Sub-Ster Room 2 | 73.9856 | 0.75 | 1.2 | 0.94 | 62.5918
Jan.Clo. | 53.7394 | 0.5 | 1.2 | 0.94 | 30.309
Clean Up Room | 167.83 | 0.5 | 1.2 | 0.94 | 94.6561
Sterile instrument supply Storage Area | 97.2192 | 0.75 | 1.2 | 0.94 | 82.2474
Anesthesia Office and Storage | 227.7691 | 0.75 | 1.2 | 0.94 | 192.6927
DR-1 | 36.4 | 0.5 | 1.2 | 0.94 | 20.5296
DR-2 | 36.4 | 0.5 | 1.2 | 0.94 | 20.5296
DR-3 | 36.4 | 0.5 | 1.2 | 0.94 | 20.5296
Lounge Area | 536.9273 | 0.75 | 1.2 | 0.94 | 454.2405
Recovery Room | 610.6646 | 0.75 | 1.2 | 0.94 | 516.6223
Hallway | 8903.9175 | 0.75 | 1.2 | 0.94 | 7532.7142
|  |  |  | Total | 16958.0662
THIRD FLOOR
SPACE | W | Fu | Fb | CLF | Qs (W)
5-Bed Ward 1 | 445.5997 | 0.75 | 1.2 | 0.94 | 376.9773
5-Bed Ward 2 | 445.38 | 0.75 | 1.2 | 0.94 | 376.7915
Waiting Area 1 | 486.3131 | 0.5 | 1.2 | 0.94 | 274.2806
Waiting Area 2 | 486.3131 | 0.5 | 1.2 | 0.94 | 274.2806
5-Bed Ward 3 | 445.38 | 0.75 | 1.2 | 0.94 | 376.7915
5-Bed Ward 4 | 445.38 | 0.75 | 1.2 | 0.94 | 376.7915
Isolation Room 1 | 131.8109 | 0.75 | 1.2 | 0.94 | 111.512
Private Room 1 | 180.9886 | 0.75 | 1.2 | 0.94 | 153.1164
Private Room 2 | 180.3594 | 0.75 | 1.2 | 0.94 | 152.5841
Chief Nurse | 399.256 | 0.5 | 1.2 | 0.94 | 225.1804
Treatment Room | 233.2369 | 0.5 | 1.2 | 0.94 | 131.5456
Nurse Station | 296.777 | 0.75 | 1.2 | 0.94 | 251.0733
Dirty Utility | 62.2297 | 0.5 | 1.2 | 0.94 | 35.0976
Clean Linen | 31.9553 | 0.5 | 1.2 | 0.94 | 18.0228
Private Room 3 | 180.3555 | 0.75 | 1.2 | 0.94 | 152.5808
Private Room 4 | 180.6064 | 0.75 | 1.2 | 0.94 | 152.793
Isolation Room 2 | 132.2308 | 0.75 | 1.2 | 0.94 | 111.8673
Private Room 5 | 206.2047 | 0.75 | 1.2 | 0.94 | 174.4492
Privaate Room 6 | 206.2047 | 0.75 | 1.2 | 0.94 | 174.4492
3-Bed Ward 1 | 322.179 | 0.75 | 1.2 | 0.94 | 272.5634
3-Bed Ward 2 | 323.5817 | 0.75 | 1.2 | 0.94 | 273.7501
Private Room 7 | 177.8569 | 0.75 | 1.2 | 0.94 | 150.4669
Private Room 8 | 178.7656 | 0.75 | 1.2 | 0.94 | 151.2357
Private Room 9 | 208.1456 | 0.75 | 1.2 | 0.94 | 176.0912
Private Room 10 | 208.1456 | 0.75 | 1.2 | 0.94 | 176.0912
Private Room 11 | 178.7656 | 0.75 | 1.2 | 0.94 | 151.2357
Private Room 12 | 178.7656 | 0.75 | 1.2 | 0.94 | 151.2357
Waiting Area | 305.2777 | 0.75 | 1.2 | 0.94 | 258.2649
Private Room 13 | 139.8436 | 0.75 | 1.2 | 0.94 | 118.3077
Private Room 14 | 147.095 | 0.75 | 1.2 | 0.94 | 124.4424
Solarium 1 | 173.0079 | 0.5 | 1.2 | 0.94 | 97.5765
Stretcher's Wheelchair Nook 1 | 144.1336 | 1 | 1.2 | 0.94 | 162.5827
Stretcher's Wheelchair Nook 2 | 107.575 | 1 | 1.2 | 0.94 | 121.3446
Solarium 2 | 175.0775 | 0.5 | 1.2 | 0.94 | 98.7437
Water Tank | 2391.2694 | 0.75 | 1.2 | 0.94 | 2023.0139
Chapel | 765.1813 | 1 | 1.2 | 0.94 | 863.1245
Male Toilet | 226.7876 | 0.75 | 1.2 | 0.94 | 191.8623
Female Toilet | 227.2478 | 0.75 | 1.2 | 0.94 | 192.2516
Waiting Area | 566.6882 | 0.5 | 1.2 | 0.94 | 319.6121
Admitting | 141.7078 | 0.75 | 1.2 | 0.94 | 119.8848 | 342.0378
Billing | 140.1803 | 0.75 | 1.2 | 0.94 | 118.5925
Cashier | 122.4119 | 0.75 | 1.2 | 0.94 | 103.5605
Personel's dining | 350.9454 | 0.75 | 1.2 | 0.94 | 296.8998
Hospital main lobby | 10504.1001 | 1 | 1.2 | 0.94 | 11848.6249
Private Room 15 | 145.6 | 0.75 | 1.2 | 0.94 | 123.1776
Private Room 16 | 139.1 | 0.75 | 1.2 | 0.94 | 117.6786
|  |  |  | Total | 22702.4001

## Heat Load Calculation Summary
SUMMARY OF DATA
| Qs | Ql | Qtotal
EXTERNAL WALL LOAD | #NAME? | 0 | #NAME?
GLASS LOAD | #NAME? | 5763.8469 | #NAME?
INFILTRATION LOAD | 17243.7963 | #NAME? | #NAME?
MISCELLANEOUS LOAD | 11119.6483 | 5615.984 | 16735.6323
ROOF LOAD | 33330.7627 | 0 | 33330.7627
PARTITION LOAD | 55552.5277 | 0 | 55552.5277
VENTILATION LOAD | 42537.572 | #NAME? | #NAME?
OCCUPANT LOAD | 19716.98 | 10453.36 | 30170.34
DOOR PARTITION LOAD | 3446.2925 | 0 | 3446.2925
LIGHTING LOAD | 59544.076 | 0 | 59544.076
TOTAL | #NAME? | #NAME? | #NAME?

## References (hidden)
Reference |  |  |  |  | Awning or Sliding | 2.8722
First Floor |  |  |  |  | Fixed | 2.8211 | References |  | Ground |  | Second | Third |  | ground |  |  | Second |  |  | Thirrd |  |  | Ground | Second | Third | Ground | Second | Third | Ground | Second | Third
Walls | [6 empty] | Daily Range | 8.1 | no. of changes/hr | Area (m2) | Area | no.of changes/hr | Area (m2) | Window | Door | Area | Window | Door | Wall | Window | Door | Wall | L/s-person | L/s-person | L/s-person | W | W | W | Area | Area | Area
Length | Area |  | Width | Length |  |  | Tdb | 34.5 | 0.264 | 37.4386 | 34.2769 | 0.264 | 34.2769 | 0 | 1.8 | 24 | 0 | 2.4 | 18.8 | 0 | 2.4 | 18.8 | 8 | 13 | 13 | 0.9 | 1.2 | 1.2 | 37.4386 | 34.2769 | 34.2769
4 | 4 |  | 2 | 1 |  |  |  |  | 0.264 | 9.6512 | 2.6175 | 0.2535 | 2.6175 | 0 | 0 | 11.6 | 0 | 1.4 | 14.8 | 0 | 1.4 | 14.8 | 15 | 13 | 13 | 0.9 | 0.7 | 0.7 | 9.6512 | 34.26 | 34.26
| 0 |  | 1.2 | 1 |  |  |  |  | 0.2535 | 7.8175 | 34.26 | 0.264 | 34.26 | 0 | 1.8 | 12 | 0 | 0 | 5.4 | 0 | 0 | 5.4 | 8 | 13 | 13 | 0.9 | 1.2 | 1.2 | 7.8175 | 34.29 | 37.4087
1.2 | 1.2 |  | 0.6 | 0.6 |  |  |  |  | 0.264 | 16.3095 | 2.6175 | 0.264 | 2.6175 | 0 | 0 | 12 | 0 | 2.4 | 44.8 | 0 | 2.4 | 44.8 | 2.5 | 13 | 13 | 0.8 | 0.7 | 0.7 | 16.3095 | 34.1175 | 37.4087
0.6 | 0.36 |  | 1.2 | 0.6 |  |  |  |  | 0.2535 | 2.8375 | 220.3324 | 0.2255 | 37.4087 | 0 | 0 | 11.6 | 0 | 1.4 | 14.8 | 0 | 1.4 | 14.8 | 8 | 13 | 13 | 0.9 | 1.2 | 1.2 | 18.2991 | 13.6738 | 34.26
1.2 | 0.72 |  | 1.2 | 0.6 |  |  |  |  | 0.2535 | 18.2991 | 143.2911 | 0.2255 | 37.4087 | 1.4 | 1.8 | 29.8 | 0 | 0 | 5.4 | 0 | 0 | 5.4 | 2.5 | 13 | 13 | 0.9 | 0.7 | 0.7 | 18.3464 | 13.9206 | 34.26
1.2 | 0.72 |  | 1.6 | 1 |  |  |  |  | 0.2535 | 18.3464 | 78.7574 | 0.264 | 34.26 | 0 | 1.8 | 13.48 | 0 | 2.4 | 44.6 | 0 | 2.4 | 44.8 | 8 | 13 | 13 | 0.9 | 1.2 | 1.2 | 23.3886 | 13.8754 | 10.1393
1.6 | 1.6 |  | 2.2 | 1 |  |  |  |  | 0.2675 | 23.3886 | 99.6547 | 0.2535 | 2.6175 | 0 | 1.8 | 38 | 0 | 1.4 | 14.8 | 0 | 1.4 | 14.8 | 2.5 | 2.5 | 2.5 | 1.8 | 0.7 | 0.7 | 5.61 | 30.712 | 13.9222
4.4 | 4.4 |  | 1.2 | 0.6 |  |  |  |  | 0.2535 | 5.61 | 142.8801 | 0.264 | 34.26 | 0 | 1.8 | 38 | 0 | 0 | 5.4 | 0 | 0 | 5.4 | 8 | 8 | 8 | 1.8 | 1.2 | 1.2 | 42.1925 | 17.9413 | 13.8738
| 0 |  | 2 | 1 |  |  |  |  | 0.264 | 131.3 | 34.29 | 0.2535 | 2.6175 | 0 | 1.8 | 26 | 0 | 2.4 | 18.8 | 0 | 2.4 | 18.8 | 10 | 8 | 13 | 0.8 | 0.7 | 0.7 | 19.6378 | 22.829 | 30.712
1.2 | 0.72 |  | 2.75 | 1 |  |  |  |  | 0.2535 | 3.7087 | 2.6175 | 0.264 | 10.1393 | 0 | 3.6 | 22.4 | 0 | 1.4 | 14.8 | 0 | 1.4 | 14.8 | 2.5 | 2.5 | 13 | 1.6 | 1.2 | 1.2 | 31.2893 | 4.7869 | 17.9413
1.6 | 1.6 |  | 3.6 | 2.5 |  |  |  |  | 0.264 | 19.6378 | 34.1175 | 0.2535 | 2.6222 | 0 | 0 | 7.72 | 0 | 0 | 5.4 | 0 | 0 | 5.4 | 2.5 | 2.5 | 13 | 0.9 | 0.7 | 0.7 | 3.9772 | 2.4581 | 22.829
4.4 | 4.4 |  | 0.6 | 1 |  |  |  |  | 0.264 | 31.2893 | 2.6175 | 0.264 | 13.9222 | 0 | 0 | 11.2 | 0 | 2.4 | 6.68 | 0 | 2.4 | 6.68 | 2.5 | 13 | 13 | 1.8 | 1.2 | 1.2 | 20.7487 | 13.8735 | 4.7869
8.15 | 8.15 |  | 4.2 | 1 |  |  |  |  | 0.2535 | 3.9772 | 13.6738 | 0.2535 | 2.6155 | 0.6 | 1.8 | 8.8 | 0 | 1.4 | 14.8 | 0 | 1.4 | 14.8 | 2.5 | 13 | 13 | 1 | 0.7 | 0.7 | 17.9512 | 13.8928 | 2.4581
2.4 | 2.4 |  | 0.6 | 0.6 |  |  |  |  | 0.264 | 20.7487 | 2.6231 | 0.264 | 13.8738 | 0 | 1.8 | 7.72 | 0 | 0 | 5.4 | 0 | 0 | 5.4 | 2.5 | 13 | 13 | 0.9 | 0.9 | 0.9 | 18.6308 | 13.7066 | 13.8735
0.6 | 0.36 |  | 0.6 | 1 |  |  |  |  | 0.264 | 17.9512 | 13.9206 | 0.2535 | 2.6186 | 1.4 | 3.6 | 36.2 | 0 | 2.4 | 6.8 | 0 | 2.4 | 6.8 | 2.5 | 13 | 13 | 0.9 | 0.7 | 0.7 | 17.1378 | 11.0522 | 13.8928
0.6 | 0.36 |  | 1.6 | 1 |  |  |  |  | 0.264 | 18.6308 | 2.6155 | 0.264 | 30.712 | 0 | 1.8 | 5.2 | 0 | 1.4 | 14.8 | 0 | 1.4 | 14.8 | 2.5 | 13 | 13 | 0.9 | 1.2 | 1.2 | 11.6062 | 13.6813 | 10.1716
2 | 2 |  | 0.6 | 0.6 |  |  |  |  | 0.264 | 17.1378 | 13.8754 | 0.2535 | 2.6374 | 0 | 0 | 10.4 | 0 | 0 | 3 | 0 | 0 | 5.4 | 2.5 | 2.5 | 13 | 0.9 | 0.6 | 0.6 | 130.9682 | 18.7319 | 15.8619
4.8 | 4.8 |  | 4.2 | 1 |  |  |  |  | 0.264 | 11.6062 | 2.6197 | 0.264 | 17.9413 | 1.4 | 0 | 12 | 0 | 0 | 5.4 | 0 | 0 | 30.8 | 8 | 13 | 13 | 0.9 | 0.6 | 0.6 | 32.86 | 25.372 | 15.8619
0.6 | 0.36 |  | 8.4 | 1 |  |  |  |  | #REF! | 130.9682 | 30.712 | 0.2255 | 22.829 | 0 | 3.6 | 14 | 0 | 2.4 | 30.8 | 0 | 0 | 14.8 | 8 | 13 | 13 | 1.2 | 0.6 | 0.6 | 12.6775 | 25.48 | 24.783
| 0 |  | 1.4 | 1 |  |  |  |  | 0.2535 | 2.9773 | 2.6374 | 0.2535 | 2.415 | 0 | 0 | 24 | 0 | 1.4 | 14.8 | 0 | 0 | 5.4 | 2.5 | 13 | 13 | 0.9 | 1.2 | 1.2 | 14.3811 | 13.7512 | 24.8909
4.2 | 4.2 |  | 2.4 | 1 |  |  |  |  | 0.2255 | 656.179 | 17.9413 | 0.2535 | 4.7869 | 0 | 0 | 5.2 | 0 | 0 | 5.4 | 1.2 | 1.8 | 65.4 | 2.5 | 13 | 13 | 1.2 | 0.7 | 0.7 | 14.3811 | 38.4537 | 13.6813
2.8 | 2.8 |  | 2.8 | 1 |  |  |  |  | 0.2675 | 32.86 | 22.829 | 0.2535 | 2.4581 | 2.4 | 2 | 46 | 0 | 1.8 | 65.4 | 0 | 1.4 | 14.8 | 2.5 | 13 | 13 | 1.2 | 1.2 | 1.2 | 14.4356 | 25.372 | 13.7512
2.8 | 1.68 |  | 1.8 | 1 |  |  |  |  | 0.264 | 12.6775 | 2.4121 | 0.264 | 13.8735 | 0 | 0 | 22 | 0 | 1.4 | 14.8 | 0 | 0 | 14.8 | 2.5 | 13 | 13 | 1.2 | 0.7 | 0.7 | 14.4356 | 25.48 | 16.0112
2.4 | 2.4 |  | 2.4 | 1 |  |  |  |  | 0.2535 | 3.2363 | 4.7869 | 0.2535 | 2.6175 |  | 1.8 | 17.2 | 0 | 0 | 14.8 | 1.2 | 2.4 | 63.8 | 2.5 | 13 | 2.5 | 1.2 | 1.2 | 1.2 | 5.4875 | 13.7512 | 16.0112
| 0 |  | 1.73 | 1 |  |  |  |  | 0.264 | 14.3811 | 2.4581 | 0.264 | 13.8928 | 2.8 | 1.8 | 58.8 | 0 | 2.4 | 54.2 | 0 | 1.2 | 30.96 | 2.5 | 13 | 2.5 | 0.9 | 0.7 | 0.7 | 5.51 | 13.7512 | 13.7512
2.2 | 2.2 |  | 2 | 1 |  |  |  |  | 0.264 | 14.3811 | 13.8735 | 0.2535 | 2.6175 | 0 | 0 | 16.8 | 0 | 1.2 | 30.96 | 0 | 1.2 | 12.64 | 2.5 | 2.5 | 2.5 | 0.9 | 0.8 | 1.2 | 5.6363 | 21.3616 | 13.7512
| 0 |  | 0.6 | 0.6 |  |  |  |  | 0.264 | 8.9651 | 2.6175 | 0.264 | 10.1716 | 4.08 | 1.8 | 51.2 | 0 | 1.2 | 12.64 | 0 | 1.2 | 19.92 | 2.5 | 8 | 2.5 | 0.9 | 0.9 | 0.7 | 5.5203 | 31.4388 | 23.4829
0.6 | 0.36 |  | 0.6 | 0.6 |  |  |  |  | 0.264 | 14.4356 | 13.8928 | 0.2535 | 2.6213 | 2.4 | 1.8 | 48 | 0 | 1.2 | 19.92 | 0 | 2.4 | 30.8 | 2.5 | 2.5 | 2.5 | 0.9 | 0.6 | 1.2 | 9.1492 | 34.9862 | 10.7572
| 0 |  | 2.4 | 1 |  |  |  |  | 0.264 | 14.4356 | 2.6175 | 0.264 | 15.8619 | 0 | 0 | 9 | 0 | 2.4 | 30.6 | 0 | 1.4 | 14.8 | 2.5 | 8 | 8 | 0.9 | 1.2 | 0.7 | 4.9522 | 5.4111 | 11.315
| 0 |  | 1.6 | 1 |  |  |  |  | 0.264 | 5.4875 | 13.7066 | 0.2535 | 2.64 | 0 | 1.8 | 21.6 | 0 | 1.4 | 14.8 | 0 | 0 | 5.4 | 8 | 2.5 |  | 0.9 | 0.7 | 1.2 | 25.2538 | 25.7486 | 13.3083
14 | 14 | [7 empty] | 0.264 | 5.51 | 2.6213 | 0.264 | 15.8619 | 0 | 0 | 12.2 | 0 | 0 | 5.4 | 0 | 2.4 | 6.8 | 2.5 | 2.5 |  | 1.2 | 1.2 | 0.7 | 14.3811 | 16.7994 | 11.0872
| 0 | [7 empty] | 0.264 | 5.6363 | 11.0522 | 0.2535 | 2.64 | 0 | 0 | 5.8 | 0 | 2.4 | 6.8 | 0 | 1.4 | 14.8 | 2.5 | 2.5 |  | 1.2 | 0.7 | 1.2 | 14.3811 | 16.7999 | 8.275
[9 empty] | 0.2535 | 5.5203 | 13.6813 | 0.264 | 24.783 | 0 | 0 | 14.6 | 0 | 1.4 | 14.8 | 0 | 0 | 5.4 | 2.5 | 15 |  | 1.2 | 1.2 | 0.7 | 10.418 | 10.2258 | 13.4675
Third Floor | [8 empty] | 0.264 | 9.1492 | 2.64 | 0.2535 | 2.64 | 0 | 1.8 | 6.64 | 0 | 0 | 5.4 | 0 | 2.4 | 6.72 | 8 | 8 |  | 0.8 | 0.7 | 1.2 | 9.9805 | 19.0007 | 183.9438
Wall | [8 empty] | 0.264 | 4.9522 | 18.7319 | 0.264 | 24.8909 | 0 | 1.8 | 6.4 | 0 | 2.4 | 6.72 | 0 | 1.4 | 14.8 | 2.5 | 2.5 |  | 1.2 | 1.2 | 0.7 | 14.4356 | 14.9875 | 58.8601
Doors | Windows | Wall Length | Width | Length |  |  |  |  | 0.264 | 25.2538 | 6.9296 | 0.2535 | 2.64 | 0 | 2.4 | 18.4 | 0 | 1.4 | 14.8 | 0 | 0 | 5.4 | 8 | 15 |  | 1.2 | 0.7 | 1.2 | 14.4356 | 21.6006 | 17.4452
0 | 0 | 6.5 | 2.31 | 1 |  |  |  |  | 0.264 | 14.3811 | 25.372 | 0.264 | 13.6813 | 0 | 0 | 6 | 0 | 0 | 5.4 | 0 | 2.4 | 6.8 |  | 2.5 |  | 0.9 | 1 | 0.7 | 656.179 | 23.6003 | 17.4806
0 | 4.6 | 6 | 2.31 | 1 |  |  |  |  | 0.264 | 14.3811 | 2.6087 | 0.2535 | 2.64 | 0 | 0 | 6.8 | 0 | 0 | 12 | 0 | 1.4 | 14.8 |  | 2.5 |  | 0.9 | 1.2 | 1.2 | 8.431 | 35.0425 | 43.5914
0 | 4.6 | 6 | 2.31 | 1 |  |  |  |  | 0.264 | 10.418 | 6.6151 | 0.264 | 13.7512 | 1.4 | 1.8 | 12.6 | 0 | 1.6 | 12 | 0 | 0 | 5.4 |  | 2.5 |  | 1 | 0.7 | 0.7 | 8.3137 | 5.6912 | 10.9006
0 | 0 | 10.23 | 2.31 | 1 |  |  |  |  | 0.264 | 9.9805 | 25.48 | 0.2535 | 2.64 | 0 | 0 | 14.32 | 0 | 1.8 | 12 | 0 | 2.4 | 6.8 |  | 2.5 |  | 0.8 | 1.2 | 1.2 | 8.4375 | 4.1338 | 10.7831
0 | 0 | 17 | 2.7 | 1 |  |  |  |  | 0.264 | 14.4356 | 2.6087 | 0.264 | 16.0112 | 0 | 0 | 19.4 | 0 | 1.2 | 10.8 | 0 | 1.4 | 14.8 |  | 2.5 |  | 0.9 | 0.7 | 0.7 | 13.607 | 12.91 | 9.4163
0 | 0 | 10.23 | 1.4 | 1 |  |  |  |  | 0.264 | 14.4356 | 13.7512 | 0.2535 | 2.64 | 0 | 2.4 | 24.12 | 0 | 2 | 24 | 0 | 0 | 5.4 |  | 8 |  | 0.9 | 1.2 | 1.2 | 17.2599 | 7.4784 | 26.9958
0 | 4.6 | 6 | 1.4 | 1 |  |  |  |  | #REF! | 14.3639 | 2.64 | 0.264 | 16.0112 | 0 | 1.8 | 12 | 0 | 1.8 | 15 | 0 | 2.4 | 6.8 |  | 8 |  | 0.9 | 0.7 | 0.7 | 17.1267 | 17.5207 | 808.0077
0 | 4.6 | 6 | 1.4 | 1 |  |  |  |  | 0.264 | 8.431 | 38.4537 | 0.2535 | 2.64 | 0 | 1.8 | 12 | 0 | 0 | 12 | 0 | 1.4 | 14.8 |  |  |  | 0.9 | 1.2 | 1.2 | 8.5711 | 2.8
0 | 0 | 6.5 | 1.4 | 1 |  |  |  |  | 0.2535 | 8.3137 | 25.372 | 0.264 | 8.9651 | 0 | 0 | 8.88 | 0 | 1.2 | 11.6 | 0 | 0 | 5.4 |  |  |  | 0.9 | 0.7 | 0.7 | 13.5984 | 2.8
0 | 2.7 | 3.1 | 1.4 | 1 |  |  |  |  | 0.2535 | 8.4375 | 2.6087 | 0.264 | 13.7512 | 1.4 | 0 | 12.12 | 0 | 0 | 15.32 | 0 | 2.4 | 6.8 |  |  |  | 0.9 | 0.9 | 1.2 | 17.0428 | 2.8
0 | 1.4 | 3.7 | 3.35 | 1 |  |  |  |  | 0.264 | 13.607 | 25.48 | 0.2535 | 2.64 | 0 | 2 | 40 | 0 | 1.4 | 14.8 | 0 | 1.4 | 14.8 |  |  |  | 0.9 | 0.6 | 0.7 | 10.4417 | 41.3021
0 | 1.4 | 2.35 | 2.4 | 1 |  |  |  |  | 0.2535 | 17.2599 | 2.6087 | 0.264 | 13.7512 | 1.2 | 2.4 | 32 | 0 | 2.4 | 53.92 | 0 | 0 | 5.4 |  |  |  | 0.6 | 1 | 1.2 | 11.5919 | 46.9742
0 | 0 | 3 | 2.4 | 1 |  |  |  |  | 0.264 | 17.1267 | 13.7512 | 0.2535 | 2.64 | 1.2 | 2.4 | 22 | 0 | 0 | 5.4 | 0.8 | 2.4 | 15 |  |  |  | 0.6 | 0.9 | 0.7 | 19.0769 | 684.9167
0 | 1.4 | 3 | 2.4 | 1 |  |  |  |  | 0.264 | 8.5711 | 2.64 | 0.2255 | 23.4829 | 1.2 | 2.4 | 32 | 0 | 1.4 | 14.8 | 0 | 0 | 15.2 |  |  |  | 0.9 | 1.6 | 1.2 | 34.2152
0 | 1.4 | 3 | 2.23 | 1 |  |  |  |  | 0.264 | 35.3177 | 13.7512 | 0.264 | 10.7572 | 1.2 | 2.4 | 12.56 | 0 | 2.4 | 57.08 | 0 | 2.4 | 44.48 |  |  |  | 1.2 | 0.9 | 0.7 | 2.5941
0 | 1.4 | 3 | 0.6 | 0.6 |  |  |  |  | 0.264 | 13.5984 | 2.64 | 0.2535 | 2.64 | 0 | 0 | 19.2 | 0 | 0 | 5.4 | 0 | 1.4 | 14.8 |  |  |  | 1.2 | 0.7 | 1.2 | 1.9625
0 | 1.4 | 3 | 2.4 | 1 |  |  |  |  | 0.2535 | 17.0428 | 21.3616 | 0.264 | 11.315 | 1.2 | 1.6 | 19.2 | 0 |  | 36.16 | 0 | 0 | 9.4 |  |  |  | 0.9 | 1 | 0.7 | 5.7184
0 | 3.35 | 3.75 | 1.2 | 0.6 |  |  |  |  | 0.264 | 10.4417 | 1.6646 | 0.2535 | 2.64 | 1.2 | 1.6 | 21.44 | 0 | 1.4 | 14.8 | 0 | 0 | 9.4 |  |  |  | 1.2 | 1.6 | 1.2 | 9.225
0 | 0 | 3 | 1.2 | 0.6 |  |  |  |  | 0.264 | 11.5919 | 31.4388 | 0.264 | 13.3083 | 1.2 | 1.6 | 12 | 0 | 1.6 | 48.6 | 0 | 0 | 5.4 |  |  |  | 0.8 | 0.8 | 1.2 | 38.0325
0 | 2.4 | 3.9 | [6 empty] | 0.264 | 19.0769 | 34.9862 | 0.2255 | 11.0872 | 1.2 | 1.6 | 31.44 | 0 | 0 | 5.4 | 0 | 2.4 | 27.16 |  |  |  | 2 | 0.9 | 1.6 | 50.8881
0 | 2.4 | 3.9 | 3.35 | 1 |  |  |  |  | 0.2535 | 2.5344 | 5.4111 | 0.2255 | 8.275 | 1.2 | 1.6 | 31.44 | 0 | 1.4 | 14.8 | 0 | 1.4 | 14.84 |  |  |  | 1.2 | 1.6 | 1.6 | 27.0056
0 | 2.4 | 3.2 | 1.4 | 1 |  |  |  |  | 0.2535 | 34.2152 | 25.7486 | 0.264 | 13.4675 | 1.8 | 1.8 | 27.6 | 0 | 2.4 | 58.48 | 0 | 0 | 5.44 |  |  |  | 0.9 | 0.9 | 0.9 | 181.6992
0 | 2.23 | 2.48 | 1.4 | 1 |  |  |  |  | 0.2535 | 2.5941 | 3.863 | 0.2535 | 183.9438 | 1.95 | 1.8 | 15.6 | 0 | 0 | 5.4 | 0 | 2.4 | 26.76 |  |  |  |  | 0.7 | 0.9
0 | 0.6 | 1.88 | 1.4 | 1 |  |  |  |  | 0.2535 | 1.9625 | 16.7994 | 0.2255 | 58.8601 | 1.88 | 1.8 | 15.6 | 0 | 2.4 | 6.8 | 0 | 1.4 | 14.76 |  |  |  |  | 1
0 | 0.6 | 1.5 | 1.4 | 1 |  |  |  |  | 0.264 | 5.7184 | 16.7999 | 0.2535 | 17.4452 | 3 | 1.8 | 72 | 0 | 1.4 | 14.8 | 0 | 0 | 5.36 |  |  |  |  | 0.8
0 | 2.4 | 5.7 | 1.4 | 1 |  |  |  |  | 0.264 | 9.225 | 10.2258 | 0.2535 | 17.4806 | 2.4 | 0 | 19.2 | 0 | 0 | 5.4 | 0 | 0 | 27.04 |  |  |  |  | 0.9
0 | 0 | 4.8 | 0.6 | 0.6 |  |  |  |  | 0.2535 | 1.945 | 19.0007 | 0.264 | 43.5914 | 0 | 0 | 12 | 0 | 2.4 | 6.8 | 0 | 0 | 9.4 |  |  |  |  | 0.8
0 | 1.2 | 3 | [6 empty] | 0.2535 | 38.0325 | 14.9875 | 0.264 | 10.9006 | 2.4 | 1.8 | 19.2 | 0 | 1.4 | 14.8 | 0 | 2.4 | 44.6 |  |  |  |  | 0.9
0 | 1.2 | 3 | [6 empty] | 0.2535 | 50.8881 | 1.68 | 0.264 | 10.7831 | 0 | 0 | 12 | 0 | 0 | 5.4 | 0 | 1.4 | 14.8 |  |  |  |  | 0.6
0 |  | 6 | [6 empty] | 0.264 | 27.0056 | 21.6006 | 0.264 | 9.4163 | 1.2 | 1.8 | 36 | 0 | 2.4 | 6.8 | 0 | 0 | 9.4 |  |  |  |  | 0.6
0 | 0 | 12 | [6 empty] | 0.2535 | 2.5344 | 23.6003 | 0.2535 | 26.9958 | 1.2 | 1.8 | 36 | 0 | 1.4 | 14.8 | 0 | 0 | 5.4 |  |  |  |  | 0.6
0 | 0 | 15.4 | [6 empty] | 0.2535 | 2.28 | 35.0425 | 0.2535 | 2.64 | 1.4 | 1.8 | 27.04 | 0 | 0 | 5.4 | 0 | 2.4 | 26.76 |  |  |  |  | 1.6
0 | 0 | 2.22 | [6 empty] | 0.2535 | 181.6992 | 5.6912 | 0.2255 | 628.0183 | 0 | 0 | 25.2 | 0 | 2.4 | 6.8 | 0 | 1.4 | 14.8 |  |  |  |  | 0.6
0 | 3.33 | 3.75 | [8 empty] | 4.1338 |  |  | 0 | 1.8 | 13.6 | 0 | 1.4 | 14.8 | 0 | 0 | 5.4
0 | 1.4 | 3 | [8 empty] | 12.91 |  |  | 0 | 1.8 | 27.4 | 0 | 0 | 5.4 | 0 | 2.4 | 27.24
0 | 1.4 | 3 | [8 empty] | 7.4784 |  |  | 0 | 2.4 | 46.4 | 0 | 0 | 6.2 | 0 | 1.4 | 14.8
0 | 1.4 | 3 | [8 empty] | 17.5207 |  |  | 0 | 1.8 | 13.6 | 0 | 1.8 | 8.4 | 0 | 0 | 5.4
0 | 1.4 | 3 | [8 empty] | 2.8 |  |  | 0 | 4 | 28.12 | 0 | 3.2 | 33.8 | 0 | 2.4 | 6.8
0 | 0 | 2.22 | [8 empty] | 2.8 |  |  | 2.8 | 2.4 | 33.8 | 0 | 0 | 12 | 0 | 1.4 | 14.8
0 | 1.4 | 3.7 | [8 empty] | 2.8 |  |  | 0 | 6.6 | 105.04 | 0.8 | 0 | 12 | 0 | 0 | 5.4
0 | 0.6 | 2.35 | [8 empty] | 41.3021 |  |  | 0 | 0 | 12.12 | 1.6 | 5.2 | 45.8 | 0 | 2.4 | 6.8
2.5 | 0 | 3.1 | [8 empty] | 46.9742 |  |  | 0 | 1.2 | 7.32 | 2.4 | 0 | 18 | 0 | 1.4 | 14.8
[11 empty] | 2.0901 |  |  | 0 | 1.2 | 17.96 | 2.4 | 0 | 18.32 | 0 | 0 | 5.4
[14 empty] | 0 | 0 | 8 | 0.8 | 1.6 | 11.4 | 0 | 2.4 | 6.8
[14 empty] | 0 | 0 | 12.92 | 0 | 0 | 15.6 | 0 | 1.4 | 14.8
[14 empty] | 0 | 0 | 5.04 | 0 | 0 | 48 | 0 | 0 | 5.4
[14 empty] | 0 | 0 | 6.8 | 1.4 | 1.8 | 8.6 | 0 | 2.4 | 6.8
[14 empty] | 0 | 0 | 5.4 | 1.4 | 1.8 | 52 | 0 | 1.4 | 14.8
[14 empty] | 0 | 1.6 | 6.52 | 3.8 | 2 | 58.52 | 0 | 0 | 5.4
[17 empty] | 0 | 0.6 | 17.6 | 0.8 | 2.4 | 15
[17 empty] | 0 | 1.8 | 25.92 | 0 | 3.2 | 56
[17 empty] | 0 | 0 | 12 | 0 | 3.2 | 12
[17 empty] | 0 | 3.2 | 27.8 | 0 | 0 | 12
[17 empty] | 0 | 1.2 | 13.16 | 0 | 0 | 22.4
[17 empty] | 0 | 3.2 | 39.4 | 0 | 1.8 | 36.72
[17 empty] | 0 | 1.8 | 9 | 0 | 1.8 | 12.52
[17 empty] | 0 | 0 | 9 | 0 | 5 | 21.4
[17 empty] | 0.8 | 0 | 11.52
[17 empty] | 0 | 2 | 9
[17 empty] | 0 | 1.4 | 18.2
[17 empty] | 0 | 1.6 | 11.52
[17 empty] | 0.8 | 1.8 | 25.12
[17 empty] | 0 | 1.2 | 6.2
[17 empty] | 0 | 1.2 | 6.2
[17 empty] | 0 | 1.2 | 24.2
[17 empty] | 0 | 3.4 | 64
Note on E60: Adrian: Hallway

## Pipe Sizing Third Floor
Space | Q(L/s) | GPM | Damter (in) | Diameter (mm)
3rd floor | 4.2506 | 67.3736 | 2.5 | 63.5
Personel Dinning | 0.8968 | 14.2146 | 1.25 | 31.75
Admitting | 0.0714 | 1.1317 | 0.25 | 6.35
Billing | 0.0714 | 1.1317 | 0.25 | 6.35
Cashier | 0.0714 | 1.1317 | 0.25 | 6.35
Private Room 13 | 0.0714 | 1.1317 | 0.25 | 6.35
Private Room 14 | 0.0714 | 1.1317 | 0.25 | 6.35
Private Room 7 | 0.107 | 1.696 | 0.375 | 9.525
Private Room 8 | 0.107 | 1.696 | 0.375 | 9.525
Private Room 11 | 0.107 | 1.696 | 0.375 | 9.525
Private Room 12 | 0.107 | 1.696 | 0.375 | 9.525
3-Bed Ward 2 | 0.1784 | 2.8277 | 0.5 | 12.7
Treatment Room | 0.1427 | 2.2618 | 0.375 | 9.525
Chief Nurse | 0.2141 | 3.3936 | 0.5 | 12.7
3-Bed Ward 1 | 0.1784 | 2.8277 | 0.5 | 12.7
Private Room 5 | 0.107 | 1.696 | 0.375 | 9.525
Private Room 9 | 0.107 | 1.696 | 0.375 | 9.525
Private Room 6 | 0.107 | 1.696 | 0.375 | 9.525
Private Room 10 | 0.107 | 1.696 | 0.375 | 9.525
Private Room 16 | 0.0714 | 1.1317 | 0.25 | 6.35
Private Room 15 | 0.0714 | 1.1317 | 0.25 | 6.35
5-Bed Ward 2 | 0.107 | 1.696 | 0.375 | 9.525
| 0.107 | 1.696 | 0.375 | 9.525
Private Room 1 | 0.107 | 1.696 | 0.375 | 9.525
Private Room 2 | 0.107 | 1.696 | 0.375 | 9.525
5-Bed Ward 1 | 0.107 | 1.696 | 0.375 | 9.525
| 0.107 | 1.696 | 0.375 | 9.525
5 BED WARD 3 | 0.107 | 1.696 | 0.375 | 9.525
| 0.107 | 1.696 | 0.375 | 9.525
5 BED WARD 4 | 0.107 | 1.696 | 0.375 | 9.525
| 0.107 | 1.696 | 0.375 | 9.525
Private Room 3 | 0.107 | 1.696 | 0.375 | 9.525
Private Room 4 | 0.107 | 1.696 | 0.375 | 9.525

## Pipe Sizing Second Floor
SPACE | Q (L/s) | GPM | Diameter (in) | Diameter ((mm)
2ND FLOOR | 8.12 | 128.705 | 3.5 | 88.9
auto clave area | 0.1302 | 2.0637 | 0.375 | 9.525
| 0.1302 | 2.0637 | 0.375 | 9.525
Sterile supply room | 0.0696 | 1.1032 | 0.25 | 6.35
| 0.0696 | 1.1032 | 0.25 | 6.35
Lounge Area | 0.2604 | 4.1274 | 0.75 | 19.05
| 0.2604 | 4.1274 | 0.75 | 19.05
Pathologic Nursery | 0.2604 | 4.1274 | 0.75 | 19.05
Pre-mature nursery | 0.2604 | 4.1274 | 0.75 | 19.05
Anesthesia Office & Storage | 0.1113 | 1.7641 | 0.375 | 9.525
Clean up room | 0.0557 | 0.88287 | 0.25 | 6.35
3-Bed Ward 3 | 0.3472 | 5.5032 | 0.75 | 19.05
3-Bed Ward 4 | 0.3472 | 5.5032 | 0.75 | 19.05
Private Room 5 | 0.1736 | 2.7516 | 0.5 | 12.7
Private Room 6 | 0.1736 | 2.7516 | 0.5 | 12.7
Private Room 7 | 0.1736 | 2.7516 | 0.5 | 12.7
Private Room 8 | 0.1736 | 2.7516 | 0.5 | 12.7
5-Bed Ward 3 | 0.217 | 3.4395 | 0.5 | 12.7
| 0.217 | 3.4395 | 0.5 | 12.7
5-Bed Ward 4 | 0.217 | 3.4395 | 0.5 | 12.7
| 0.217 | 3.4395 | 0.5 | 12.7
Private Room 3 | 0.1736 | 2.7516 | 0.5 | 12.7
Private Room 4 | 0.1736 | 2.7516 | 0.5 | 12.7
Chief Nurse | 0.434 | 6.8791 | 1 | 25.4
Treatment Room | 0.2604 | 4.1274 | 0.75 | 19.05
5-Bed Ward 1 | 0.217 | 3.4395 | 0.5 | 12.7
| 0.217 | 3.4395 | 0.5 | 12.7
5-Bed Ward 2 | 0.217 | 3.4395 | 0.5 | 12.7
| 0.217 | 3.4395 | 0.5 | 12.7
Private Room 1 | 0.1736 | 2.7516 | 0.5 | 12.7
Private Room 2 | 0.1736 | 2.7516 | 0.5 | 12.7
reception | 0.1736 | 2.7516 | 0.5 | 12.7
Chief of Hospital | 0.1302 | 2.0637 | 0.375 | 9.525
| 0.1302 | 2.0637 | 0.375 | 9.525
Conference Room | 0.2604 | 4.1274 | 0.75 | 19.05
| 0.2604 | 4.1274 | 0.75 | 19.05
Chief of Clinics | 0.1732 | 2.7453 | 0.5 | 12.7
| 0.1732 | 2.7453 | 0.5 | 12.7
3-Bed Ward 1 | 0.3472 | 5.5032 | 0.75 | 19.05
3-Bed Ward 2 | 0.3472 | 5.5032 | 0.75 | 19.05

## Pipe Sizing Ground Floor
Space | Q (L/s) | GPM | Diameter (in) | Diameter (mm)
Ground Floor | 6.78 | 107.4655 | 3 | 76.2
OPD clinic Ob-gyne | 0.1061 | 1.6817 | 0.375 | 9.525
Ultrasound | 0.0708 | 1.1222 | 0.25 | 6.35
OPD records | 0.0708 | 1.1222 | 0.25 | 6.35
OPD info. And admitting | 0.0708 | 1.1222 | 0.25 | 6.35
Canteen | 0.082278 | 1.3041 | 0.375 | 9.525
| 0.082278 | 1.3041 | 0.375 | 9.525
| 0.082278 | 1.3041 | 0.375 | 9.525
| 0.082278 | 1.3041 | 0.375 | 9.525
| 0.082278 | 1.3041 | 0.375 | 9.525
| 0.082278 | 1.3041 | 0.375 | 9.525
| 0.082278 | 1.3041 | 0.375 | 9.525
| 0.082278 | 1.3041 | 0.375 | 9.525
| 0.082278 | 1.3041 | 0.375 | 9.525
Staff Dining | 0.07075 | 1.1214 | 0.25 | 6.35
| 0.07075 | 1.1214 | 0.25 | 6.35
Administrative office | 0.1061 | 1.6817 | 0.375 | 9.525
Dietary | 0.05305 | 0.84086 | 0.25 | 6.35
| 0.05305 | 0.84086 | 0.25 | 6.35
Dietician's Office | 0.0708 | 1.1222 | 0.25 | 6.35
Cooking Area | 0.1543 | 2.4457 | 0.5 | 12.7
Admin Office | 0.0708 | 1.1222 | 0.25 | 6.35
Social Welfare | 0.0708 | 1.1222 | 0.25 | 6.35
OPD Clinic Medical 1 | 0.0708 | 1.1222 | 0.25 | 6.35
OPD Clinic Medical 2 | 0.0708 | 1.1222 | 0.25 | 6.35
OPD clinic surgery 1 | 0.0708 | 1.1222 | 0.25 | 6.35
OPD clinic surgery 2 | 0.0708 | 1.1222 | 0.25 | 6.35
OPD clinic dental 1 | 0.0708 | 1.1222 | 0.25 | 6.35
OPD clinic dental 2 | 0.0708 | 1.1222 | 0.25 | 6.35
OPD Clinic Pedia 1 | 0.0708 | 1.1222 | 0.25 | 6.35
OPD Clinic Pedia 2 | 0.0708 | 1.1222 | 0.25 | 6.35
Cashier | 0.0708 | 1.1222 | 0.25 | 6.35
Billing | 0.0708 | 1.1222 | 0.25 | 6.35
Admitting | 0.0708 | 1.1222 | 0.25 | 6.35
OPD info. And admitting | 0.0708 | 1.1222 | 0.25 | 6.35
OPD records | 0.0708 | 1.1222 | 0.25 | 6.35
Pharmacy | 0.0708 | 1.1222 | 0.25 | 6.35
Medical Records Office | 0.0354 | 0.5611 | 0.125 | 3.175
| 0.0354 | 0.5611 | 0.125 | 3.175
PHILHEALTH | 0.0708 | 1.1222 | 0.25 | 6.35
Linen storage | 0.0617 | 0.97797 | 0.25 | 6.35
Control Booth | 0.0354 | 0.5611 | 0.125 | 3.175
| 0.0354 | 0.5611 | 0.125 | 3.175
Radiologist Office | 0.0708 | 1.1222 | 0.25 | 6.35
Dark Room | 0.0708 | 1.1222 | 0.25 | 6.35
Supply Room | 0.1061 | 1.6817 | 0.375 | 9.525
Maintenance Office | 0.0708 | 1.1222 | 0.25 | 6.35
AHU | 3.3461 | 53.0369 | 2.5 | 63.5
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## Summary of Piping Calculation
| L/s | GPM | Nominal Diamater (in) | Nominal Diameter (m) | Inside Diameter (in) | Inside Diameter (m) | Velocity (ft/s) | pres grad (ft/100ft) | Velocity (m/s) | Pressure Gradient (Pa/m) | Equivalent Length of Pipe | Pressure Drop (Pa)
chiller - pump | 19.1489 | 303.5172 | 5 | 0.127 | 5.047 | 0.12819 | 4.87 | 1.641 | 1.4843 | 160.935 | 2 | 321.87
pump - A | 19.1489 | 303.5172 | 5 | 0.127 | 5.047 | 0.12819 | 4.87 | 1.641 | 1.4843 | 160.935 | 2 | 321.87
A-B | 14.8983 | 236.1436 | 4 | 0.1016 | 4.026 | 0.10226 | 5.95 | 3.157 | 1.8135 | 309.611 | 4 | 1238.4442
B-C | 6.78 | 107.4655 | 3 | 0.0762 | 3.068 | 0.077927 | 4.66 | 2.793 | 1.4203 | 273.9131 | 4 | 1095.6524
C-D | 6.78 | 107.4655 | 3 | 0.0762 | 3.068 | 0.077927 | 4.66 | 2.793 | 1.4203 | 273.9131 | 6.6 | 1807.8265
D-E | 6.6 | 104.6125 | 3 | 0.0762 | 3.068 | 0.077927 | 4.54 | 2.656 | 1.3837 | 260.4773 | 0.45 | 117.2148
E-F | 6.6 | 104.6125 | 3 | 0.0762 | 3.068 | 0.077927 | 4.49 | 2.603 | 1.3685 | 255.2796 | 2.85 | 727.5467
F-G | 6.46 | 102.3934 | 3 | 0.0762 | 3.068 | 0.077927 | 4.44 | 2.552 | 1.3532 | 250.2779 | 4.55 | 1138.7645
G-H | 5.68 | 90.0301 | 3 | 0.0762 | 3.068 | 0.077927 | 3.91 | 2.008 | 1.1917 | 196.9271 | 2.7 | 531.7033
H-I | 4.96 | 78.6178 | 3 | 0.0762 | 3.068 | 0.077927 | 3.41 | 1.562 | 1.0393 | 153.1873 | 5.1 | 781.2555
I-J | 4.82 | 76.3988 | 3 | 0.0762 | 3.068 | 0.077927 | 3.32 | 1.482 | 1.0119 | 145.3416 | 1.2 | 174.41
J-K | 4.68 | 74.1797 | 3 | 0.0762 | 3.068 | 0.077927 | 3.22 | 1.401 | 0.98141 | 137.3979 | 6.4 | 879.3464
K-L | 4.57 | 72.4362 | 3 | 0.0762 | 3.068 | 0.077927 | 3.14 | 1.343 | 0.95703 | 131.7097 | 1.25 | 164.6372
L-M | 4.47 | 70.8512 | 3 | 0.0762 | 3.068 | 0.077927 | 3.07 | 1.289 | 0.93569 | 126.4139 | 2.75 | 347.6382
M-N | 4.25 | 67.3641 | 3 | 0.0762 | 3.068 | 0.077927 | 2.92 | 1.175 | 0.88997 | 115.2338 | 6.15 | 708.6876
N-O | 4.18 | 66.2546 | 3 | 0.0762 | 3.068 | 0.077927 | 2.88 | 1.14 | 0.87778 | 111.8013 | 3.25 | 363.3541
O-P | 4.1 | 64.9865 | 3 | 0.0762 | 3.068 | 0.077927 | 2.82 | 1.1 | 0.85949 | 107.8784 | 0.75 | 80.9088
P-Q | 3.96 | 62.7675 | 3 | 0.0762 | 3.068 | 0.077927 | 2.72 | 1.032 | 0.82902 | 101.2096 | 3.3 | 333.9916
Q-R | 3.82 | 60.5484 | 3 | 0.0762 | 3.068 | 0.077927 | 2.63 | 0.966 | 0.80158 | 94.7369 | 8.55 | 810.0002
R-S | 3.61 | 57.2198 | 3 | 0.0762 | 3.068 | 0.077927 | 2.48 | 0.871 | 0.75587 | 85.4201 | 3.35 | 286.1573
S-T | 3.5 | 55.4763 | 3 | 0.0762 | 3.068 | 0.077927 | 2.41 | 0.823 | 0.73453 | 80.7127 | 6.05 | 488.3116
T-AHU | 3.43 | 54.3668 | 3 | 0.0762 | 3.068 | 0.077927 | 2.36 | 0.793 | 0.71929 | 77.7705 | 10.15 | 789.3709
|  |  |  | 0 | [7 empty] | 13508.9615

## Cooling Capacity
Ground Floor at 24°C
Space | Volume | Area | A/C Capacity | Cooling Capacity (KW) | Cooling Capacity (TOR) | TOR | Estimated kW
Canteen | 726.7968 | 181.6992 | 59.0828 | 40.2386 | 11.4422 | 12 | 42.2004
Storage Room | 31.27 | 7.8175 | 59.0828 | 1.7312 | 0.49229 | 1 | 3.5167
Equipment and supply storage area | 22.44 | 5.61 | 59.0828 | 1.2424 | 0.35328 | 1 | 3.5167
Film File storage | 22.0812 | 5.5203 | 59.0828 | 1.2225 | 0.34763 | 1 | 3.5167
Linen storage | 33.2548 | 8.3137 | 59.0828 | 1.8411 | 0.52354 | 1 | 3.5167
Cooking Area | 136.8608 | 34.2152 | 59.0828 | 7.5772 | 2.1546 | 2.5 | 8.7918
Cadaver Holding room | 78.5512 | 19.6378 | 59.0828 | 4.3489 | 1.2367 | 1.5 | 5.2751
Bulk storage | 15.9088 | 3.9772 | 59.0828 | 0.88078 | 0.25046 | 1 | 3.5167
266.7909
Ground Floor at 22°C
Space | Volume | Area | A/C Capacity | Cooling Capacity (KW) | Cooling Capacity (TOR) | TOR | Estimated kW
Minor Operating Room | 93.5544 | 23.3886 | 17.8804 | 7.4348 | 2.1141 | 2.5 | 8.7918
Work Area (laboratory) | 131.44 | 32.86 | 17.8804 | 10.4456 | 2.9703 | 3 | 10.5501
56.2486
Ground Floor at 22.5°
Space | Volume | Area | A/C Capacity | Cooling Capacity (KW) | Cooling Capacity (TOR) | TOR | Estimated kW
Maintenance Office | 65.238 | 16.3095 | 92.4161 | 2.2765 | 0.63917 | 1 | 3.5167
Examination / treatment area | 525.2 | 131.3 | 92.4161 | 18.3274 | 5.1457 | 6 | 21.1002
Supply Room | 125.1572 | 31.2893 | 92.4161 | 4.3675 | 1.2262 | 1.5 | 5.2751
Pharmacy | 82.9948 | 20.7487 | 92.4161 | 2.8962 | 0.81315 | 1 | 3.5167
Medical Records Office | 71.8048 | 17.9512 | 92.4161 | 2.5057 | 0.70351 | 1 | 3.5167
PHILHEALTH | 68.5512 | 17.1378 | 92.4161 | 2.3922 | 0.67164 | 1 | 3.5167
Doctor's Duty | 46.4248 | 11.6062 | 92.4161 | 1.62 | 0.45485 | 1 | 3.5167
OPD clinic dental 1 | 57.5244 | 14.3811 | 92.4161 | 2.0074 | 0.5636 | 1 | 3.5167
OPD clinic dental 2 | 57.5244 | 14.3811 | 92.4161 | 2.0074 | 0.5636 | 1 | 3.5167
OPD clinic surgery 1 | 57.7424 | 14.4356 | 92.4161 | 2.015 | 0.56574 | 1 | 3.5167
OPD clinic surgery 2 | 57.7424 | 14.4356 | 92.4161 | 2.015 | 0.56574 | 1 | 3.5167
Cashier | 21.95 | 5.4875 | 92.4161 | 0.76597 | 0.21506 | 1 | 3.5167
Billing | 22.04 | 5.51 | 92.4161 | 0.76911 | 0.21594 | 1 | 3.5167
Admitting | 22.5452 | 5.6363 | 92.4161 | 0.78674 | 0.22089 | 1 | 3.5167
Radiologist Office | 36.5968 | 9.1492 | 92.4161 | 1.2771 | 0.35856 | 1 | 3.5167
Dark Room | 19.8088 | 4.9522 | 92.4161 | 0.69125 | 0.19408 | 1 | 3.5167
Control Booth | 101.0152 | 25.2538 | 92.4161 | 3.525 | 0.9897 | 1 | 3.5167
OPD Clinic Pedia 1 | 57.5244 | 14.3811 | 92.4161 | 2.0074 | 0.5636 | 1 | 3.5167
OPD Clinic Pedia 2 | 57.5244 | 14.3811 | 92.4161 | 2.0074 | 0.5636 | 1 | 3.5167
OPD info. And admitting | 39.922 | 9.9805 | 92.4161 | 1.3931 | 0.39114 | 1 | 3.5167
OPD Clinic Medical 1 | 57.7424 | 14.4356 | 92.4161 | 2.015 | 0.56574 | 1 | 3.5167
OPD Clinic Medical 2 | 57.7424 | 14.4356 | 92.4161 | 2.015 | 0.56574 | 1 | 3.5167
Admin Office | 54.428 | 13.607 | 92.4161 | 1.8993 | 0.53326 | 1 | 3.5167
Administrative office | 141.2708 | 35.3177 | 92.4161 | 4.9298 | 1.3841 | 1.5 | 5.2751
Social Welfare | 54.3936 | 13.5984 | 92.4161 | 1.8981 | 0.53293 | 1 | 3.5167
OPD Info. And admitting | 41.7668 | 10.4417 | 92.4161 | 1.4575 | 0.40921 | 1 | 3.5167
OPD records | 46.3676 | 11.5919 | 92.4161 | 1.618 | 0.45429 | 1 | 3.5167
Ultrasound | 76.3076 | 19.0769 | 92.4161 | 2.6628 | 0.74763 | 1 | 3.5167
Supply Receiving Area | 22.8736 | 5.7184 | 92.4161 | 0.7982 | 0.22411 | 1 | 3.5167
Dietician's Office | 36.9 | 9.225 | 92.4161 | 1.2877 | 0.36153 | 1 | 3.5167
Dietary | 152.13 | 38.0325 | 92.4161 | 5.3087 | 1.4905 | 1.5 | 5.2751
Staff Dining | 203.5524 | 50.8881 | 92.4161 | 7.1032 | 1.9943 | 2 | 7.0334
OPD clinic Ob-gyne | 108.0224 | 27.0056 | 92.4161 | 3.7695 | 1.0584 | 1.5 | 5.2751
| 2648.3288 | 662.0822
Second Floor 24°C
Space | Volume | Area | A/C Capacity | Cooling Capacity (KW) | Cooling Capacity (TOR) | TOR | Estimated kW
Dirty Utility | 19.1476 | 4.7869 | 26.0704 | 1.9357 | 0.54348 | 1 | 3.5167
Clean Linen | 9.8324 | 2.4581 | 26.0704 | 0.99401 | 0.27908 | 1 | 3.5167 | 33.1554
Sub-Ster Room 1 | 21.6444 | 5.4111 | 26.0704 | 2.1881 | 0.61435 | 1 | 3.5167 | 9.3089
Sterile supply room | 86.4024 | 21.6006 | 26.0704 | 8.7348 | 2.4524 | 2.5 | 8.7918
Sub-Ster Room 2 | 22.7648 | 5.6912 | 26.0704 | 2.3014 | 0.64615 | 1 | 3.5167
Jan.Clo. | 16.5352 | 4.1338 | 26.0704 | 1.6716 | 0.46933 | 1 | 3.5167
Clean up room | 51.64 | 12.91 | 26.0704 | 5.2205 | 1.4657 | 1 | 3.5167
Sterile Instrument Supply Storage Area | 29.9136 | 7.4784 | 26.0704 | 3.0241 | 0.84906 | 1 | 3.5167
Anesthesia Office & Storage | 70.0828 | 17.5207 | 26.0704 | 7.085 | 1.9892 | 2 | 7.0334
64.4701
Second Floor at 22°C
Space | Volume | Area | A/C Capacity | Cooling Capacity (KW) | Cooling Capacity (TOR) | TOR | Estimated kW
Delivery Room | 139.9448 | 34.9862 | 38.1972 | 15.0105 | 4.2684 | 5 | 17.5835 | 38.1972
Pre-operation area | 76.0028 | 19.0007 | 38.1972 | 8.1521 | 2.3181 | 2.5 | 8.7918 | 10.8617
Major Operating Room | 140.17 | 35.0425 | 38.1972 | 15.0347 | 4.2752 | 5 | 17.5835
89.0294
Second Floor at 22.5°C
Space | Volume | Area | A/C Capacity | Cooling Capacity (KW) | Cooling Capacity (TOR) | TOR | Estimated kW
5 Bed Ward 1 |  | 34.2769 | 160.1533 | 7.491 | 2.1301 | 2.5 | 8.7918
5-Bed Ward 2 | 137.04 | 34.26 | 160.1533 | 7.4873 | 2.1291 | 2.5 | 8.7918 | 160.1533
5-Bed Ward 3 | 137.16 | 34.29 | 160.1533 | 7.4939 | 2.1309 | 2.5 | 8.7918 | 45.5408
5-Bed Ward 4 | 136.47 | 34.1175 | 160.1533 | 7.4562 | 2.1202 | 2.5 | 8.7918
Isolation Room 1 | 54.6952 | 13.6738 | 160.1533 | 2.9883 | 0.84976 | 1 | 3.5167
Private Room 1 | 55.6824 | 13.9206 | 160.1533 | 3.0423 | 0.86509 | 1 | 3.5167
Private Room 2 | 55.5016 | 13.8754 | 160.1533 | 3.0324 | 0.86228 | 1 | 3.5167
Chief Nurse | 122.848 | 30.712 | 160.1533 | 6.7119 | 1.9086 | 2.5 | 8.7918
Treatment Room | 71.7652 | 17.9413 | 160.1533 | 3.921 | 1.115 | 1.5 | 5.2751
Private Room 3 | 55.494 | 13.8735 | 160.1533 | 3.032 | 0.86217 | 1 | 3.5167
Private Room 4 | 55.5712 | 13.8928 | 160.1533 | 3.0362 | 0.86337 | 1 | 3.5167
Isolation Room 2 | 54.8264 | 13.7066 | 160.1533 | 2.9955 | 0.85179 | 1 | 3.5167
Reception | 44.2088 | 11.0522 | 160.1533 | 2.4154 | 0.68684 | 1 | 3.5167
Private Room 5 | 54.7252 | 13.6813 | 160.1533 | 2.99 | 0.85022 | 1 | 3.5167
Chief of Hospital | 74.9276 | 18.7319 | 160.1533 | 4.0938 | 1.1641 | 1.5 | 5.2751
3-Bed Ward 1 | 101.488 | 25.372 | 160.1533 | 5.5449 | 1.5767 | 2 | 7.0334
3-Bed Ward 2 | 101.92 | 25.48 | 160.1533 | 5.5685 | 1.5835 | 2 | 7.0334
Private Room 6 | 55.0048 | 13.7512 | 160.1533 | 3.0053 | 0.85457 | 1 | 3.5167
Conference Room | 153.8148 | 38.4537 | 160.1533 | 8.4039 | 2.3897 | 3 | 10.5501
3-Bed Ward 3 | 101.488 | 25.372 | 160.1533 | 5.5449 | 1.5767 | 2 | 7.0334
3-Bed Ward 4 | 101.92 | 25.48 | 160.1533 | 5.5685 | 1.5835 | 2 | 7.0334
Private Room 7 | 55.0048 | 13.7512 | 160.1533 | 3.0053 | 0.85457 | 1 | 3.5167
Private Room 8 | 55.0048 | 13.7512 | 160.1533 | 3.0053 | 0.85457 | 1 | 3.5167
Chief of Clinics | 85.4464 | 21.3616 | 160.1533 | 4.6685 | 1.3275 | 2 | 7.0334
Labor Room | 102.9944 | 25.7486 | 160.1533 | 5.6272 | 1.6001 | 2 | 7.0334
Pathologic Nursery | 67.1976 | 16.7994 | 160.1533 | 3.6714 | 1.044 | 1.5 | 5.2751
Pre-mature nursery | 67.1996 | 16.7999 | 160.1533 | 3.6715 | 1.044 | 1.5 | 5.2751
Breastfeeding room | 40.9032 | 10.2258 | 160.1533 | 2.2348 | 0.63548 | 1 | 3.5167
Autoclave area | 59.95 | 14.9875 | 160.1533 | 3.2754 | 0.9314 | 1.5 | 5.2751
Lounge Area | 165.2084 | 41.3021 | 160.1533 | 9.0264 | 2.5667 | 3 | 10.5501
Recovery Room | 187.8968 | 46.9742 | 160.1533 | 10.266 | 2.9192 | 4 | 14.0668
Work Area (inside) |  | 23.6003 | 160.1533 | 5.1577 | 1.4666 | 2 | 7.0334
Sterile Supply room |  | 21.6001 | 160.1533 | 4.7206 | 1.3423 | 2 | 7.0334
732.8166
Third Floor at 24°C
Space | Volume | Area | A/C Capacity | Cooling Capacity (KW) | Cooling Capacity (TOR) | TOR | Estimated kW
Personel's dining | 107.9832 | 26.9958 | 47.4593 | 47.4593 | 13.4954 | 14 | 49.2338
Third Floor at 22°C
NO SPACE AT 22°C
Third Floor at 22.5°C
Space | Volume | Area | A/C Capacity | Cooling Capacity (KW) | Cooling Capacity (TOR) | TOR | Estimated kW
5-Bed Ward 1 | 137.1076 | 34.2769 | 159.5619 | 10.2847 | 2.9245 | 3 | 10.5501
5-Bed Ward 2 | 137.04 | 34.26 | 159.5619 | 10.2797 | 2.9231 | 3 | 10.5501
5-Bed Ward 3 | 137.04 | 34.26 | 159.5619 | 10.2797 | 2.9231 | 3 | 10.5501
5-Bed Ward 4 | 137.04 | 34.26 | 159.5619 | 10.2797 | 2.9231 | 3 | 10.5501
Isolation Room 1 | 40.5572 | 10.1393 | 159.5619 | 3.0423 | 0.8651 | 1 | 3.5167
Private Room 1 | 55.6888 | 13.9222 | 159.5619 | 4.1773 | 1.1879 | 1.5 | 5.2751
Private Room 2 | 55.4952 | 13.8738 | 159.5619 | 4.1628 | 1.1837 | 1.5 | 5.2751
Chief Nurse | 122.848 | 30.712 | 159.5619 | 9.2151 | 2.6204 | 3 | 10.5501
Treatment Room | 71.7652 | 17.9413 | 159.5619 | 5.3833 | 1.5308 | 2 | 7.0334
Private Room 3 | 55.494 | 13.8735 | 159.5619 | 4.1627 | 1.1837 | 1.5 | 5.2751
Private Room 4 | 55.5712 | 13.8928 | 159.5619 | 4.1685 | 1.1853 | 1.5 | 5.2751
Isolation Room 2 | 40.6864 | 10.1716 | 159.5619 | 3.052 | 0.86785 | 1 | 3.5167
Private Room 5 | 63.4476 | 15.8619 | 159.5619 | 4.7593 | 1.3534 | 1.5 | 5.2751
Private Room 6 | 63.4476 | 15.8619 | 159.5619 | 4.7593 | 1.3534 | 1.5 | 5.2751
3-Bed Ward 1 | 99.132 | 24.783 | 159.5619 | 7.4361 | 2.1145 | 2.5 | 8.7918
3-Bed Ward 2 | 99.5636 | 24.8909 | 159.5619 | 7.4685 | 2.1237 | 2.5 | 8.7918
Private Room 7 | 54.7252 | 13.6813 | 159.5619 | 4.1051 | 1.1673 | 1.5 | 5.2751
Private Room 8 | 55.0048 | 13.7512 | 159.5619 | 4.126 | 1.1733 | 1.5 | 5.2751
Private Room 9 | 64.0448 | 16.0112 | 159.5619 | 4.8041 | 1.3661 | 1.5 | 5.2751
Private Room 10 | 64.0448 | 16.0112 | 159.5619 | 4.8041 | 1.3661 | 1.5 | 5.2751
Private Room 11 | 55.0048 | 13.7512 | 159.5619 | 4.126 | 1.1733 | 1.5 | 5.2751
Private Room 12 | 55.0048 | 13.7512 | 159.5619 | 4.126 | 1.1733 | 1.5 | 5.2751
Private Room 13 | 43.0288 | 10.7572 | 159.5619 | 3.2277 | 0.91782 | 1 | 3.5167
Private Room 14 | 45.26 | 11.315 | 159.5619 | 3.3951 | 0.96541 | 1 | 3.5167
Solarium 1 | 53.2332 | 13.3083 | 159.5619 | 3.9931 | 1.1355 | 1.5 | 5.2751
Solarium 2 | 53.87 | 13.4675 | 159.5619 | 4.0409 | 1.1491 | 1.5 | 5.2751
Admitting | 43.6024 | 10.9006 | 159.5619 | 3.2707 | 0.93005 | 1 | 3.5167
Billing | 43.1324 | 10.7831 | 159.5619 | 3.2355 | 0.92003 | 1 | 3.5167
Cashier | 37.6652 | 9.4163 | 159.5619 | 2.8253 | 0.80341 | 1 | 3.5167
Private Room 16 | 42.8 | 10.7 | 159.5619 | 3.2105 | 0.91294 | 1 | 3.5167
Private Room 15 | 44.8 | 11.2 | 159.5619 | 3.3605 | 0.9556 | 1 | 3.5167
531.7864

## Ducting Calculations
DUCTING CALCULATIONS
Space | TOR | KW | L/s | m3/s | Diameter | Velocity | Pressure Gradient | Equivalent length | Pressure Drop | Size of Duct | Size of Diffuser
Minor Operating Room | 2.5 | 8.7918 | 504.409 | 0.50441 | 300 | 5.7 | 1.187 | 35.98 | 42.7083 | 400x250 | 450x450
Examination/treatment and observation area | 6 | 21.1002 | 1210.5817 | 1.2106 | 600 | 4.282 | 0.324 | 38.82 | 12.5777 | 650x475 | 450x450
Cadaver Holding Room | 1.5 | 5.2751 | 302.6454 | 0.30265 | 300 | 4.284 | 0.8 | 7.33 | 5.864 | 325x225 | 450x450
Work Area laboratory | 3 | 10.5501 | 605.2908 | 0.60529 | 350 | 6.297 | 1.37 | 22.01 | 30.1537 | 400x250 | 375x375
Space | TOR | KW | L/s | m3/s | Diameter | Velocity | Pressure Gradient | Equivalent length | Pressure Drop | Size of Duct | Size of Diffuser
Delivery Room | 5 | 17.5835 | 1008.8181 | 1.0088 | 450 | 6.347 | 1.02 | 110.46 | 112.6692 | 400x425 | 600x600
Major Operating Room | 5 | 17.5835 | 1008.8181 | 1.0088 | 450 | 6.347 | 1.02 | 109.76 | 111.9552 | 400x425 | 600x600
Labor Room | 2 | 7.0334 | 403.5272 | 0.40353 | 350 | 4.182 | 0.63 | 100.1 | 63.063 | 400x250 | 375x375
Work Area (inside) | 2 | 7.0334 | 403.5272 | 0.40353 | 350 | 4.182 | 0.63 | 92.8 | 58.464 | 400x250 | 375x375
Breastfeeding room | 1 | 3.5167 | 201.7636 | 0.20176 | 250 | 4.113 | 0.93 | 87.95 | 81.7935 | 250x175 | 300x300
Pre-operation area | 2.5 | 8.7918 | 504.409 | 0.50441 | 300 | 5.7 | 1.187 | 84.35 | 100.1234 | 400x250 | 450x450
Recovery room | 4 | 14.0668 | 807.0544 | 0.80705 | 400 | 6.411 | 1.2 | 86.62 | 103.944 | 425x325 | 525x525
Isolation room 1 | 1 | 3.5167 | 201.7636 | 0.20176 | 250 | 4.113 | 0.93 | 14.48 | 13.4664 | 250x175 | 375x375
Isolation room 2 | 1 | 3.5167 | 201.7636 | 0.20176 | 250 | 4.113 | 0.93 | 60.25 | 56.0325 | 250x175 | 300x300
Space | TOR | KW | L/s | m3/s | Diameter | Velocity | Pressure Gradient | Equivalent length | Pressure Drop | Size of Duct | Size of Diffuser
Isolation room 1 | 1 | 3.5167 | 201.7636 | 0.20176 | 250 | 4.113 | 0.93 | 18.35 | 17.0655 | 250x175 | 300x300
Isolation room 2 | 1 | 3.5167 | 201.7636 | 0.20176 | 250 | 4.113 | 0.93 | 65.58 | 60.9894 | 250x175 | 300x300
870.8698
Main duct |  |  | 7767.899 |  | 900 | 11.955 | 1.334 |  |  | 900x850

## Equipment Schedule AHU & FCU
EQUIPMENT SCHEDULE
TABLE
TAG no. | Quantity | Description | Brand/Model | Capacity | No. of Indoor units connected | Electrical Data |  |  | Remarks
[6 empty] | V | ϕ | Hz
CH-1 | 1 | Air Cooled Chiller | Carrier/0700A | 668.1 kW | 96 | --- | --- | --- | See attached catalogue for equipment detailed specification
TABLE
TAG no. | Quantity | Description | Brand/Model | Capacity | No. of Indoor units connected | Electrical Data |  |  | Remarks
[6 empty] | V | ϕ | Hz
AHU | 1 | 39G Air Handling Unit | Carrier/Y SM-B | 668.1 kW | 15 | --- | --- | --- | See attached catalogue for equipment detailed specification
TABLE
Schedule of Outdoor Unit for Third Floor
TAG no. | Quantity | Description | Brand/Model | Capacity (TOR) | Area Served | Electrical Data |  |  | Remarks
[6 empty] | V | ϕ | Hz
FCU-C1 | 2 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 3 | 5- BedWard 1 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C2 | 2 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 3 | 5- BedWard 2 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C3 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1.5 | Private Room 1 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C4 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1.5 | Private Room 2 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C5 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1.5 | Private Room 3 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C6 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1.5 | Private Room 4 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C7 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1.5 | Private Room 5 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C8 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1.5 | Private Room 6 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C9 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 3 | Chief Nurse | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C10 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 2.5 | 3- Bed Ward 1 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C11 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1.5 | Private Room 7 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C12 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1.5 | Private Room 8 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C13 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 2 | Treatment Room | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C14 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 2.5 | 3- Bed Ward 2 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C15 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1.5 | Private Room 9 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C16 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1.5 | Private Room 10 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C17 | 2 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 3 | 5- BedWard 3 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C18 | 2 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 3 | 5- BedWard 4 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C19 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1.5 | Private Room 10 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C20 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1.5 | Private Room 11 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C21 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1.5 | Private Room 12 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C22 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Private Room 13 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C23 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Private Room 14 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C24 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Private Room 15 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C25 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Private Room 16 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C26 | 3 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 2 | Waiting Area | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C27 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Admitting | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C28 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Billing | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C29 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Cashier | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-C30 | 2 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 3.5 | Personel's Dining | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
TABLE
Schedule of Outdoor Unit for Second Floor
TAG no. | Quantity | Description | Brand/Model | Capacity (TOR) | Area Served | Electrical Data |  |  | Remarks
[6 empty] | V | ϕ | Hz
FCU-B1 | 2 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 2.5 | 5-Bed Ward 1 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B2 | 2 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 2.5 | 5-Bed Ward 2 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B3 | 2 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 2.5 | 5-Bed Ward 3 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B4 | 2 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 2.5 | 5-Bed Ward 4 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B5 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Private Room 1 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B6 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Private Room 2 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B7 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 2.5 | Chief Nurse | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B8 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1.5 | Treatment Room | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B9 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Private Room 3 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B10 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Private Room 4 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B11 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Private Room 5 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B12 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Private Room 6 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B13 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Private Room 7 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B14 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Private Room 8 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B15 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Reception | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B16 | 2 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 2 | Chief of Hospital | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B17 | 2 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 2 | Conference Room | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B18 | 2 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 2 | Chief of Clinics | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B19 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | 3-Bed Ward 1 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B20 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 2 | 3-Bed Ward 2 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B21 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 2 | 3-Bed Ward 3 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B22 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | 3-Bed Ward 4 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B23 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | CSSR | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B24 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Autoclave Area | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B25 | 2 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 2 | Sterile Room | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B26 | 2 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 2 | Lounge Area | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B27 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Pre-Mature Nursery | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B28 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Pathologic Nursery | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B29 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Anesthesia Office | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-B30 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Clean-up Room | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
TABLE
Schedule of Outdoor Unit for Ground Floor
TAG no. | Quantity | Description | Brand/Model | Capacity (TOR) | Area Served | Electrical Data |  |  | Remarks
[6 empty] | V | ϕ | Hz
FCU-A1 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1..5 | Supply Room | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A2 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Maintenance Office | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A3 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Pharmacy | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A4 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Medical Record's Office | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A5 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Medical Records | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A6 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | PHILHEALTH | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A7 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Doctor's on Duty | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A8 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | OPD clinic dental 1 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A9 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | OPD clinic dental 2 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A10 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | OPD Clinic Pedia 1 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A11 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | OPD Clinic Pedia 2 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A12 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Radiologist Office | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A13 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Dark Room | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A14 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | X-ray Room | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A15 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Linen Office | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A16 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 2.5 | Cooking Area | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A17 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Dietician's Office | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A18 | 2 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1.5 | Dietary | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A19 | 2 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Staff Dining | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A20 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1.5 | Administrative Office | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A21 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Social Welfare | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A22 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Admin's Office | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A23 | 9 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1.5 | Canteen | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A24 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | OPD Clinic OB-gyne | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A25 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Ultrasound | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A26 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | OPD Records | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A27 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | OPD info and admitting | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A28 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Cashier | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A29 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Billing | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A30 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | Admitting | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A31 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | OPD Clinic Medical 1 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A32 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | OPD Clinic Medical 2 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A33 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | OPD Clinic Surgery 1 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A34 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | OPD Clinic Surgery 2 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A35 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | OPD info and admitting | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
FCU-A36 | 1 | Ceiling Casette Chilled Water Fan Coil Unit | Daikin/FWMJCC2BV1 | 1 | OPD Records | 230 | 60 | 1 | See attached catalogue for equipment detailed specification

## Equipment Schedule Diffuser
TAG no. | Quantity | Description | Brand/Model | Capacity(L/S) | Area Served | Electrical Data |  |  | Remarks
[6 empty] | V | ϕ | Hz
D-1 | 1 | Flange Horizontal Blow Diffuser | OC WaterLoo/DF | 504.409 | Minor Operating Room | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
D-2 | 1 | Flange Horizontal Blow Diffuser | OC WaterLoo/DF | 1210.582 | Examination or Treatment Area | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
D-3 | 1 | Flange Horizontal Blow Diffuser | OC WaterLoo/DF | 302.6454 | Cadaver Holding Room | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
D-4 | 2 | Flange Horizontal Blow Diffuser | OC WaterLoo/DF | 605.2908 | Work Area Laboratory | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
D-5 | 2 | Flange Horizontal Blow Diffuser | OC WaterLoo/DF | 1008.818 | Delivery Room | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
D-6 | 1 | Flange Horizontal Blow Diffuser | OC WaterLoo/DF | 1008.818 | Major Operating room | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
D-7 | 1 | Flange Horizontal Blow Diffuser | OC WaterLoo/DF | 403.5272 | Labor Room | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
D-8 | 2 | Flange Horizontal Blow Diffuser | OC WaterLoo/DF | 403.5272 | Work Area Inside | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
D-9 | 1 | Flange Horizontal Blow Diffuser | OC WaterLoo/DF | 201.7636 | Breastfeeding room | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
D-10 | 1 | Flange Horizontal Blow Diffuser | OC WaterLoo/DF | 504.409 | Pre-operation Area | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
D-11 | 2 | Flange Horizontal Blow Diffuser | OC WaterLoo/DF | 807.0544 | Recovery Room | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
D-12 | 1 | Flange Horizontal Blow Diffuser | OC WaterLoo/DF | 201.7636 | Isolation Room 1 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
D-13 | 1 | Flange Horizontal Blow Diffuser | OC WaterLoo/DF | 201.7636 | Isolation Room 2 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
D-14 | 1 | Flange Horizontal Blow Diffuser | OC WaterLoo/DF | 201.7636 | Isolation Room 3 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification
D-15 | 1 | Flange Horizontal Blow Diffuser | OC WaterLoo/DF | 201.7636 | Isolation Room 4 | 230 | 60 | 1 | See attached catalogue for equipment detailed specification

## Summary of TOR
SUMMARY of A/C Capacity for each floor
FLOOR | DESIGN TEMPERATURE
| 24°C | 22.5°C | 22°C
GROUND FLOOR | 59.0828 kW | 92.4161 kW | 17.8804 kW
| 16.0086 TOR | 25.9472 TOR | 5.0844 TOR
SECOND FLOOR | 33.1554 kW | 160.153 kW | 38.1973 kW
| 9.3089 TOR | 45.5408 TOR | 10.8617 TOR
THIRD FLOOR | 47.4593 kW | 159.5619 kW
| 13.4954 TOR | 45.3726 TOR | -----
|  | TOTAL : | 607.9062 kW
172.8627 TOR

## Exhaust Calculations
EXHAUST L/S CALCULATION
First Floor
Space | Volume (m^3) | ACH | Exhaust m^3/s | Exhaust L/s
Maintenance office CR | 11.35 | 10 | 0.031528 | 31.5278
Examination/Treatment CR | 14.8348 | 10 | 0.041208 | 41.2078
Nurse Station (ER) CR | 11.9092 | 10 | 0.033081 | 33.0811
Waiting Area CR | 12.9452 | 10 | 0.035959 | 35.9589
Male Toilet | 69.0396 | 10 | 0.19178 | 191.7767
Female Toilet | 68.1712 | 10 | 0.18936 | 189.3644
Ultrasound CR | 10.1376 | 10 | 0.02816 | 28.16
Cooking Area | 136.8608 | 10 | 0.38017 | 380.1689
Dietician's office CR | 7.78 | 10 | 0.021611 | 21.6111
OPD clinic ob-gyne CR | 10.1376 | 10 | 0.02816 | 28.16
Washing Area CR | 9.6 | 10 | 0.026667 | 26.6667
Cadaver Holding Room | 78.5512 | 10 | 0.2182 | 218.1978
Second Floor
Space | Volume (m^3) | ACH | Exhaust m^3/s | Exhaust L/s
5-BedWard 1 CR | 10.47 | 10 | 0.029083 | 29.0833
5-BedWard 2CR | 10.47 | 10 | 0.029083 | 29.0833
5-BedWard 3 CR | 10.47 | 10 | 0.029083 | 29.0833
5-BedWard 4 CR | 10.47 | 10 | 0.029083 | 29.0833
Isolation Room 1 CR | 10.4924 | 10 | 0.029146 | 29.1456
Isolation Room 2 CR | 10.4852 | 10 | 0.029126 | 29.1256
Private Room 1 CR | 10.462 | 10 | 0.029061 | 29.0611
Private Room 2 CR | 10.4788 | 10 | 0.029108 | 29.1078
Chief Nurse CR | 10.5496 | 10 | 0.029304 | 29.3044
Nurse Station CR | 9.6484 | 10 | 0.026801 | 26.8011
Private Room 3 CR | 10.47 | 10 | 0.029083 | 29.0833
Private Room 4 CR | 10.47 | 10 | 0.029083 | 29.0833
Private Room 5 CR | 10.56 | 10 | 0.029333 | 29.3333
Chief of Hospital CR | 27.1784 | 10 | 0.075496 | 75.4956
3-Bed Ward 1 CR | 10.4348 | 10 | 0.028986 | 28.9856
3-Bed Ward 2 CR | 10.4348 | 10 | 0.028986 | 28.9856
3-Bed Ward 3 CR | 10.4348 | 10 | 0.028986 | 28.9856
3-Bed Ward 4 CR | 10.4348 | 10 | 0.028986 | 28.9856
Private Room 6 CR | 10.56 | 10 | 0.029333 | 29.3333
Private Room 7 CR | 10.56 | 10 | 0.029333 | 29.3333
Private Room 8 CR | 10.56 | 10 | 0.029333 | 29.3333
Chief of Clinics CR | 6.6584 | 10 | 0.018496 | 18.4956
Labor Room CR | 15.452 | 10 | 0.042922 | 42.9222
Autoclave Area CR | 6.72 | 10 | 0.018667 | 18.6667
DR-1 | 11.2 | 10 | 0.031111 | 31.1111
DR-2 | 11.2 | 10 | 0.031111 | 31.1111
DR-3 | 11.2 | 10 | 0.031111 | 31.1111
Recovery Room CR | 8.3604 | 10 | 0.023223 | 23.2233
THIRD FLOOR
Space | Volume (m^3) | ACH | Exhaust L/s | Exhaust m^3/s
5-BedWard 1 CR | 10.47 | 10 | 0.029083 | 29.0833
5-BedWard 2 CR | 10.47 | 10 | 0.029083 | 29.0833
5-BedWard 3 CR | 10.47 | 10 | 0.029083 | 29.0833
5-BedWard 4 CR | 10.47 | 10 | 0.029083 | 29.0833
Private Room 1 CR | 10.462 | 10 | 0.029061 | 29.0611
Private Room 2 CR | 10.4744 | 10 | 0.029096 | 29.0956
Chief Nurse CR | 10.5496 | 10 | 0.029304 | 29.3044
Nurse Station CR | 9.66 | 10 | 0.026833 | 26.8333
Private Room 3 CR | 10.47 | 10 | 0.029083 | 29.0833
Private Room 4 CR | 10.47 | 10 | 0.029083 | 29.0833
Isolation Room 1 CR | 10.4888 | 10 | 0.029136 | 29.1356
Isolation Room 2 CR | 10.4852 | 10 | 0.029126 | 29.1256
Private Room 5 CR | 10.56 | 10 | 0.029333 | 29.3333
Private Room 6 CR | 10.56 | 10 | 0.029333 | 29.3333
3-BedWard 1 CR | 10.56 | 10 | 0.029333 | 29.3333
3-BedWard 2 CR | 10.56 | 10 | 0.029333 | 29.3333
Private Room 7 CR | 10.56 | 10 | 0.029333 | 29.3333
Private Room 8 CR | 10.56 | 10 | 0.029333 | 29.3333
Private Room 9 CR | 10.56 | 10 | 0.029333 | 29.3333
Private Room 10 CR | 10.56 | 10 | 0.029333 | 29.3333
Private Room 11 CR | 10.56 | 10 | 0.029333 | 29.3333
Private Room 12 CR | 10.56 | 10 | 0.029333 | 29.3333
Private Room 13 CR | 10.56 | 10 | 0.029333 | 29.3333
Private Room 14 CR | 10.56 | 10 | 0.029333 | 29.3333
Male Toilet | 69.7808 | 10 | 0.19384 | 193.8356
Female Toilet | 69.9224 | 10 | 0.19423 | 194.2289
Personel's Dining CR | 10.56 | 10 | 0.029333 | 29.3333
Private Room 15 CR | 10.8 | 10 | 0.03 | 30
Private Room 16 CR | 10.4 | 10 | 0.028889 | 28.8889

## Total Heat Calculation 1
SUMMARY OF HEAT LOAD CALCULATION FOR GROUND FLOOR AT 22 °C |  |  | SUMMARY OF HEAT LOAD CALCULATION FOR GROUND FLOOR AT 28 °C
HEAT SOURCES | Qs (W) | Ql (W) | HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 1945.6819 | 0 | External Wall | 4465.324 | 0
Glass Load | 962.044 | 0 | Glass Load | 3846.361 | 0
Infiltration Load | 257.4623 | 497.3868 | Infiltration Load | 0 | 0
Ventilation Load | 1309 | 2528.833 | Ventilation Load | 2845.6121 | 3649.7103
Lighting Load | 532.8795 | 0 | Lighting Load | 9622.209 | 0
Occupant Load | 483 | 138 | Occupant Load | 0 | 0
Wall Partition Load | 796.785 | 0 | Wall Partition Load | 0 | 0
Door Partition Load | 5.894 | 0 | Door Partition Load |  | 0
Miscellaneous Load | 723.6979 | 365.504 | Miscellaneous Load | 19.5782 | 9.888
TOTAL | 7016.4446 | 3529.7238 | TOTAL | 20799.0843 | 3659.5983
OVERALL TOTAL | 10546.1684 |  | OVERALL TOTAL | 24458.6826
SUMMARY OF HEAT LOAD CALCULATION FOR GROUND FLOOR AT 22.5°C
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 16186.7272 | 0
Glass Load | 6662.6442 | 0
Infiltration Load | 3885.6216 | 7455.7825
Ventilation Load | 5884.032 | 11457.0125
Lighting Load | 7216.6545 | 0
Occupant Load | 4845.18 | 1713.96
Wall Partition Load | 14155.42 | 0
Door Partition Load | 1130.043 | 0
Miscellaneous Load | 380.2043 | 1920.224
TOTAL | 60346.5268 | 22546.979
OVERALL TOTAL | 82893.5058
SUMMARY OF HEAT LOAD CALCULATION FOR GROUND FLOOR AT 24°C
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 16630.0345 | 0
Glass Load | 5175.5414 | 0
Infiltration Load | 1180.8 | 2558.912
Ventilation Load | 2069.76 | 4244.8882
Lighting Load | 2511.867 | 0
Occupant Load | 1104 | 36.8
Wall Partition Load | 3602.335 | 0
Door Partition Load | 11.986 | 0
Miscellaneous Load | 901.9296 | 455.52
TOTAL | 33188.2535 | 7296.1202
OVERALL TOTAL | 40484.3736

## Total Heat Calculation 2
SUMMARY OF HEAT LOAD CALCULATION FOR SECOND FLOOR AT 22 °C |  |  | SUMMARY OF HEAT LOAD CALCULATION FOR GROUND FLOOR AT 28 °C
HEAT SOURCES | Qs (W) | Ql (W) | HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 2286.793 | ___ | External Wall | 4211.4145 | 0
Glass Load | 0 | ___ | Glass Load | 883.6348 | 0
Infiltration Load | 406.8458 | 787.2558 | Infiltration Load | 2663.3 | 3421.44
Ventilation Load | 3757.6 | 7259.237 | Ventilation Load | 0 | 0
Lighting Load | 641.7098 | 0 | Lighting Load | 7532.714 | 0
Occupant Load | 3867 | 1500 | Occupant Load | 0
Wall Partition Load | 1935.096 | 0 | Wall Partition Load | 0 | 0
Door Partition Load | 110 | 0 | Door Partition Load |  | 0
Miscellaneous Load | 1474.1337 | 744.512 | Miscellaneous Load | 14.5094 | 7.328
TOTAL | 14479.1783 | 10291.0048 | TOTAL | 15305.5728 | 3428.768
OVERALL TOTAL | 24770.1831 |  | OVERALL TOTAL | 18734.3408
SUMMARY OF HEAT LOAD CALCULATION FOR SECOND FLOOR AT 22.5°C
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 18499.33 | 0
Glass Load | 11264.605 | 0
Infiltration Load | 3339.8875 | 6560.8163
Ventilation Load | 15796.7 | 30952.7564
Lighting Load | 8698.5097 | 0
Occupant Load | 3959.9 | 4052.5
Wall Partition | 15295 | 0
Door Partition | 1021.7438 | 0
Miscellaneous Load | 1927.9424 | 973.6448
TOTAL | 79803.6184 | 42539.7175
OVERALL TOTAL | 122343.3359
SUMMARY OF HEAT LOAD CALCULATION FOR SECOND FLOOR AT 24°C
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 4579.7525 | 0
Glass Load | 2949.2208 | 0
Infiltration Load | 577.8417 | 1187.028
Ventilation Load | 614.46 | 1260.2016
Lighting Load | 524.0859 | 0
Occupant Load | 938.4 | 880
Wall Partition Load | 2660.492 | 0
Door Partition Load | 98.0762 | 0
Miscellaneous Load | 68.3654 | 34.528
TOTAL | 13010.6945 | 3361.7576
OVERALL TOTAL | 16372.4521

## Total Heat Calculation 3
SUMMARY OF HEAT LOAD CALCULATION FOR THIRD FLOOR AT 22 °C |  |  | SUMMARY OF HEAT LOAD CALCULATION FORTHIRD FLOOR AT 28 °C
HEAT SOURCES | Qs (W) | Ql (W) | HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 0 | ___ | External Wall | 12290.4232 | 0
Glass Load | 0 | ___ | Glass Load | 884.5316 | 0
Infiltration Load | 0 | 0 | Infiltration Load | 1612.958 | 3819.211
Ventilation Load | 0 | 0 | Ventilation Load | 0 | 0
Lighting Load | 0 | 0 | Lighting Load | 13863.65 | 0
Occupant Load | 0 |  | Occupant Load | 0 | 0
Partition Load | 0 |  | Wall Partition Load | 0 | 0
Miscellaneous Load | 0 |  | Door Partition Load |  | 0
|  |  | Miscellaneous Load | 30.4001 | 15.3536
TOTAL | 0
OVERALL TOTAL | 0 |  | TOTAL | 28681.9629 | 3834.5646
|  |  | OVERALL TOTAL | 32516.5275
SUMMARY OF HEAT LOAD CALCULATION FOR THIRD FLOOR AT 22.5°C
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 24827.8839 | 0
Roof Load | 27420.0353 | 0
Glass Load | 11472.723 | 0
Infiltration Load | 2478.2697 | 5099.3607
Ventilation Load | 13106.018 | 26381.3026
Lighting Load | 6378.502 | 0
Occupant Load | 4519.5 | 2132.1
Wall Partition Load | 11615.785 | 0
Door Partition Load | 1000.6511 | 0
Miscellaneous Load | 2157.1739 | 1089.4816
TOTAL | 104976.5419 | 34702.2449
OVERALL TOTAL | 139678.7868
SUMMARY OF HEAT LOAD CALCULATION FOR THIRD FLOOR AT 24°C
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 11065.523 | 0
Roof Load | 5910.7248 | 0
Glass Load | 436.0549 | 0
Infiltration Load | 1170.876 | 2401.36
Ventilation Load | 620.928 | 1273.4662
Lighting Load | 2460.248 | 0
Occupant Load | 0 | 0
Wall Partition Load | 3266.075 | 0
Door Partition Load | 67.8989 | 0
Miscellaneous Load | 0 | 0
TOTAL | 24998.3287 | 3674.8262
OVERALL TOTAL | 28673.1549

## Cost Estimation
COST ESTIMATION
Chiller
Area Served | kW | Equipment | Price/unit | QTY | Total
Roofdeck | 668.1 | Air Cooled Chiller | ₱35,600 | 1 | ₱35,600
Air Handling Unit
Area Served | kW | Equipment | Price/unit | QTY | Total
Ground Floor | 610.3 | Horizontal Standard AHU | ₱50,900 | 1 | ₱50,900
Fan Coil Unit (Ground Floor)
Area Served | TOR | Equipment | Price/unit | QTY | Total
Supply Room | 1.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱49,500 | 1 | ₱49,500
Maintenance Office | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Pharmacy | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Medical Record's Office | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Medical Records | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
PHILHEALTH | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Doctor's on Duty | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
OPD clinic dental 1 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
OPD clinic dental 2 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
OPD Clinic Pedia 1 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
OPD Clinic Pedia 2 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Radiologist Office | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Dark Room | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
X-ray Room | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Linen Office | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Cooking Area | 2.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱63,500 | 1 | ₱29,500
Dietician's Office | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Dietary | 1.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱49,500 | 2 | ₱99,000
Staff Dining | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 2 | ₱59,000
Administrative Office | 1.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱49,500 | 1 | ₱49,500
Social Welfare | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Admin's Office | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Canteen | 1.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱49,500 | 9 | ₱445,500
OPD Clinic OB-gyne | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Ultrasound | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
OPD Records | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
OPD info and admitting | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Cashier | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Billing | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Admitting | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
OPD Clinic Medical 1 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
OPD Clinic Medical 2 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
OPD Clinic Surgery 1 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
OPD Clinic Surgery 2 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
OPD info and admitting | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
OPD Records | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Fan Coil Unit (Second Floor)
Area Served | TOR | Equipment | Price/unit | QTY | Total
5-Bed Ward 1 | 2.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱63,500 | 2 | ₱127,000
5-Bed Ward 2 | 2.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱63,500 | 2 | ₱127,000
5-Bed Ward 3 | 2.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱63,500 | 2 | ₱127,000
5-Bed Ward 4 | 2.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱63,500 | 2 | ₱127,000
Private Room 1 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Private Room 2 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Chief Nurse | 2.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱63,500 | 1 | ₱63,500
Treatment Room | 1.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱49,500 | 1 | ₱49,500
Private Room 3 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Private Room 4 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Private Room 5 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Private Room 6 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Private Room 7 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Private Room 8 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Reception | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Chief of Hospital | 2 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱54,500 | 2 | ₱109,000
Conference Room | 2 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱54,500 | 2 | ₱109,000
Chief of Clinics | 2 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱54,500 | 2 | ₱109,000
3-Bed Ward 1 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
3-Bed Ward 2 | 2 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱54,500 | 1 | ₱29,500
3-Bed Ward 3 | 2 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱54,500 | 1 | ₱29,500
3-Bed Ward 4 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
CSSR | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Autoclave Area | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Sterile Room | 2 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱54,500 | 2 | ₱109,000
Lounge Area | 2 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱54,500 | 2 | ₱109,000
Pre-Mature Nursery | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Pathologic Nursery | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Anesthesia Office | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Clean-up Room | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Fan Coil Unit (Third Floor)
Area Served | TOR | Equipment | Price/unit | QTY | Total
5- BedWard 1 | 3 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱67,500 | 2 | ₱135,500
5- BedWard 2 | 3 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱67,500 | 2 | ₱135,500
Private Room 1 | 1.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱49,500 | 1 | ₱49,500
Private Room 2 | 1.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱49,500 | 1 | ₱49,500
Private Room 3 | 1.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱49,500 | 1 | ₱49,500
Private Room 4 | 1.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱49,500 | 1 | ₱49,500
Private Room 5 | 1.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱49,500 | 1 | ₱49,500
Private Room 6 | 1.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱49,500 | 1 | ₱49,500
Chief Nurse | 3 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱67,500 | 1 | ₱67,500
3- Bed Ward 1 | 2.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱63,500 | 1 | ₱63,500
Private Room 7 | 1.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱49,500 | 1 | ₱49,500
Private Room 8 | 1.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱49,500 | 1 | ₱49,500
Treatment Room | 2 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱54,500 | 1 | ₱54,500
3- Bed Ward 2 | 2.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱63,500 | 1 | ₱63,500
Private Room 9 | 1.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱49,500 | 1 | ₱49,500
Private Room 10 | 1.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱49,500 | 1 | ₱49,500
5- BedWard 3 | 3 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱67,500 | 2 | ₱135,500
5- BedWard 4 | 3 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱67,500 | 2 | ₱135,500
Private Room 10 | 1.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱49,500 | 1 | ₱49,500
Private Room 11 | 1.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱49,500 | 1 | ₱49,500
Private Room 12 | 1.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱49,500 | 1 | ₱49,500
Private Room 13 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Private Room 14 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Private Room 15 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Private Room 16 | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Waiting Area | 2 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱54,500 | 3 | ₱163,500
Admitting | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Billing | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Cashier | 1 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱29,500 | 1 | ₱29,500
Personel's Dining | 3.5 | Ceiling Cassette Chilled Water Fan Coil Unit | ₱71,500 | 2 | ₱143,500