## Ground Floor
Ground Floor Plan
Name of Room | Base Area (m^2) | Base Area With Toilet | Outside Air req. (L/s-person) | Outside Air req. (L/m2) | Lighting used (W) | Lighting (W) | Equipments used | Eq. (W) | Temperature | Area
1.1 Power House | 37.4386 | [7 empty] | 1 | 22
1.2 Work Area | 9.6512 |  | 8 | 15
1.3 Storage Room | 7.8175 |  |  | 0.6 | [5 empty] | 12
1.4 Maintenance Office | 16.3095 | 2.3875 | [7 empty] | 36
1.5 Female toilet | 18.2991 | [8 empty] | 62
1.6 Male Toilet | 18.3464 | [8 empty] | 62
1.7 Minor Operating Room | 23.3886 | 12 | 15 | 30
1.8 Equipment and supply storage area | 5.61 | 11 |  | 0.6
1.9 Examination/Treatment and Observation area | 42.1925 | 3.7087 | 8 | 15
1.10 Cadaver Holding Room | 19.6378 | [8 empty] | 10
1.11 Supply Room | 31.2893 | [8 empty] | 44
1.12 Bulk Storage | 3.9772
1.13 Pharmacy | 20.7487
1.14 Medical Records Office | 17.9512
1.15 Medical Records | 18.6308 |  | 8 | 15
1.16 PHILHEALTH | 17.1378 | [8 empty] | 46
1.17 Doctor's Duty | 11.6062
1.18 Nurse Station (ER) | 88.7757+42.1925 | 2.9773
1.19 EMERGENCY ROOM | ___
1.20 E.R. Waiting area (ER) | ___
1.21 Work Area (laboratory) | 32.86 |  | 8 | 15
1.22 Pathology office
1.23 Waiting area | 12.6775 | 3.2363
1.24 OPD clinic dental 1 | 14.3811 |  | 8 | 15
1.25 OPD clinic dental 2 | 14.3811 |  | 8 | 15
1.26 Elevator | 8.9651
1.27 OPD clinic surgery 1 | 14.4356 |  | 8 | 15
1.28 OPD clinic surgery 2 | 14.4356 |  | 8 | 15
1.29 Cashier | 5.4875
1.30 Billing | 5.51
1.31 Admitting | 5.6363
1.32 Film File Storage | 5.5203 |  |  | 0.6
1.33 Radiologist Office | 9.1492
1.34 Dark Room | 4.9522
1.35 Control Booth | 25.2538
1.36 Dress Booth (xray room) | ___
1.37 OPD Clinic Pedia 1 | 14.3811
1.38 OPD Clinic Pedia 2 | 14.3811
1.39 OPD Records | 10.418 |  |  | 0.6
1.40 OPD info. And admitting | 9.9805
1.41 OPD Clinic Medical 1 | 14.4356
1.42 OPD Clinic Medical 2 | 14.4356
1.43 Hospital Main Lobby
1.44 Waste Disposal Area | 14.3639
1.45 X-RAY ROOM | ___
1.46 Pressing Area | 8.431
1.47 Linen Storage 1 | 8.3137
1.48 Linen Storage 2 | ___
1.49 Linen Office | 8.4375
1.50 Admin Office | 13.607 | [8 empty] | 19.2
1.51 Male Toilet | 17.2599 | [8 empty] | 34
1.52 Waiting Area
1.53 Washing Area | 17.1267
1.54 Receiving Sorting Area | 8.5711
1.55 Administrative office | 35.3177 | [8 empty] | 70
1.56 Social Welfare | 13.5984 | [8 empty] | 17.2
1.57 Female Toilet | 17.0428 | [8 empty] | 34
1.58 OPD Info. And admitting | 10.4417 | [8 empty] | 37.6
1.59 OPD records | 11.5919 | [8 empty] | 24
1.60 Ultrasound | 19.0769 | 2.5344 | [7 empty] | 25.6
1.61 Cooking Area | 34.2152
1.62 Dry storage | 2.5941
1.63 Cold Storage | 1.9625
1.64 Supply Receiving Area | 5.7184
1.65 Dietician's Office | 9.225 | 1.945
1.66 Dietary | 38.0325
1.67 Staff Dining | 50.8881
1.68 OPD clinic Ob-gyne | 27.0056 | 2.5344
1.69 Garbage Disposal area | 2.28
1.70 Canteen | 181.6992
DOOR: 0.9 X 0.05
Note on K16: hplaptop: wala

## Second Floor
Second Floor Plan
Name of Room | Base Area (m^2) | Base Area With Toilet | Outside Air req. (L/s-person) | Outside Air req. (L/m2) | Lighting used (W) | Lighting (W) | Equipments used | Eq. (W)
5-Bed Ward 1 | 34.2769 |  | 13 | 25
5-Bed Ward 2 | 34.26 |  | 13 | 25
Waiting Area 1 | __ |  | __ | __
Waiting Area 2 | __ |  | __ | __
5-Bed Ward 3 | 34.29 |  | 13 | 25
5-Bed Ward 4 | 34.1175 |  | 13 | 25
Canopy
Isolation Room 1 | 13.6738 |  | 8 | 15
Private Room 1 | 13.9206 |  | 13 | 25
Private Room 2 | 13.8754 |  | 13 | 25
Chief Nurse | 30.712
Stretcher's Nook
Treatment Room | 17.9413 |  | 8 | 15
Nurse Station | 22.829
Dirty Utility | 4.7869
Clean Linen | 2.4581
Private Room 3 | 13.8735 |  | 13 | 25
Private Room 4 | 13.8928 |  | 13 | 25
Isolation Room 2 | 13.7066 |  | 8 | 15
Reception | 11.0522
Private Room 5 | 13.6813 |  | 13 | 25
Chief of Hospital | 18.7319
3-Bed Ward 1 | 25.372 |  | 13 | 25
Elevator
3-Bed Ward 2 | 25.48 |  | 13 | 25
Private Room 6 | 13.7512 |  | 13 | 25
Conference Room | 38.4537 |  | 2.5 | 0.3
3-Bed Ward 3 | 25.372 |  | 13 | 25
Waiting Area
3-Bed Ward 4 | 25.48 |  | 13 | 25
Private Room 7 | 13.7512 |  | 13 | 25
Private Room 8 | 13.7512 |  | 13 | 25
Canopy 2
Canopy 3
Chief of Clinics | 21.3616
CSSR | 31.4388
Delivery Room | 34.9862
Sub-Ster Room 1 | 5.4111
Labor Room | 25.7486
Pathologic Nursery | 16.7994
Pre-mature nursery | 16.7999
Breastfeeding room | 10.2258
Pre-operation area | 19.0007 |  | 8 | 15
Autoclave area | 14.9875
Sterile supply room | 21.6006
Work Area 1 | 23.6003 |  | 8 | 15
Canopy 4
Major Operating Room | 35.0425 |  | 15 | 30
Scrub-up area
Sub-Ster Room 2 | 5.6912
Jan.Clo. | 4.1338
Clean up room | 12.91
Nurse Station
Sterile instrument supply storage area | 7.4784
anesthesia office and storage | 17.5207
DR-1 | 2.8
DR-2 | 2.8
DR-3 | 2.8
Lounge Area
Recovery Room | 46.9742 |  | 8 | 15

## Third Floor
Third Floor Plan
Name of Room | Base Area (m^2) | Base Area With Toilet | Outside Air req. (L/s-person) | Outside Air req. (L/m2) | Lighting used (W) | Lighting (W) | Equipments used | Eq. (W)
5-Bed Ward 1 | 34.2769 | 2.6175 | 13 | 25
5-Bed Ward 2 | 34.26 | 2.6175 | 13 | 25
Waiting Area 1 | 37.4087
Waiting Area 2 | 37.4087
5-Bed Ward 3 | 34.26 | 2.6175 | 13 | 25
5-Bed Ward 4 | 34.26 | 2.6175 | 13 | 25
Canopy
Isolation Room 1 | 10.1393 | 2.6222 | 8 | 15
Private Room 1 | 13.9222 | 2.6155 | 13 | 25
Private Room 2 | 13.8738 | 2.6186 | 13 | 25
Chief Nurse | 30.712 | 2.6374
Stretcher's Nook | ___
Treatment Room | 17.9413 |  | 8 | 15
Nurse Station | 22.829 | 2.415
Dirty Utility | 4.7869
Clean Linen | 2.4581
Private Room 3 | 13.8735 | 2.6175 | 13 | 25
Private Room 4 | 13.8928 | 2.6175 | 13 | 25
Isolation Room 2 | 10.1716 | 2.6213 | 8 | 15
Private Room 5 | 15.8619 | 2.64 | 13 | 25
Privaate Room 6 | 15.8619 | 2.64 | 13 | 25
3-Bed Ward 1 | 24.783 | 2.64 | 13 | 25
3-Bed Ward 2 | 24.8909 | 2.64 | 13 | 25
Private Room 7 | 13.6813 | 2.64 | 13 | 25
Private Room 8 | 13.7512 | 2.64 | 13 | 25
Private Room 9 | 16.0112 | 2.64 | 13 | 25
Private Room 10 | 16.0112 | 2.64 | 13 | 25
Elevator | 8.9651
Private Room 11 | 13.7512 | 2.64 | 13 | 25
Private Room 12 | 13.7512 | 2.64 | 13 | 25
Waiting Area | 23.4829
Private Room 13 | 10.7572 | 2.64 | 13 | 25
Private Room 14 | 11.315 | 2.64 | 13 | 25
Solarium 1 | 13.3083
Stretcher's Wheelchair Nook 1 | 11.0872
Stretcher's Wheelchair Nook 2 | 8.275
Solarium 2 | 13.4675
Canopy 2
Water Tank 1 | 183.9438
Water Tank 2 | ___
Chapel | 58.8601
Male Toilet | 17.4452
Female Toilet | 17.4806
Waiting Area | 43.5914
Admitting | 10.9006
Billing | 10.7831
Cashier | 9.4163
Personel's dining | 26.9958 | 2.3994

## Ground Floor (2)
Ground Floor Plan
Name of Room | Base Area (m^2) | Base Area With Toilet | Outside Air req. (L/s-person) | Outside Air req. (L/m2) | Lighting used (W) | Lighting (W) | Equipments used | Eq. (W) | Temperature
1.1 Power House | 37.4386
1.2 Work Area | 9.6512 |  | 8 | 15
1.3 Storage Room | 7.8175 |  |  | 0.6
1.4 Maintenance Office | 16.3095 | 2.3875
1.5 Female toilet | 18.2991 | [7 empty] | 25
1.6 Male Toilet | 18.3464 | [7 empty] | 25
1.7 Minor Operating Room | 23.3886 | 12 | 15 | 30
1.8 Equipment and supply storage area | 5.61 | 11 |  | 0.6
1.9 Examination/Treatment and Observation area | 42.1925 | 3.7087 | 8 | 15
1.10 Cadaver Holding Room | 19.6378
1.11 Supply Room | 31.2893
1.12 Bulk Storage | 3.9772
1.13 Pharmacy | 20.7487
1.14 Medical Records Office | 17.9512
1.15 Medical Records | 18.6308 |  | 8 | 15
1.16 PHILHEALTH | 17.1378
1.17 Doctor's Duty | 11.6062
1.18 Nurse Station (ER) | 88.7757+42.1925 | 2.9773
1.19 EMERGENCY ROOM | ___
1.20 E.R. Waiting area (ER) | ___
1.21 Work Area (laboratory) | 32.86 |  | 8 | 15
1.22 Pathology office
1.23 Waiting area | 12.6775 | 3.2363
1.24 OPD clinic dental 1 | 14.3811 |  | 8 | 15
1.25 OPD clinic dental 2 | 14.3811 |  | 8 | 15
1.26 Elevator | 8.9651
1.27 OPD clinic surgery 1 | 14.4356 |  | 8 | 15
1.28 OPD clinic surgery 2 | 14.4356 |  | 8 | 15
1.29 Cashier | 5.4875
1.30 Billing | 5.51
1.31 Admitting | 5.6363
1.32 Film File Storage | 5.5203 |  |  | 0.6
1.33 Radiologist Office | 9.1492
1.34 Dark Room | 4.9522
1.35 Control Booth | 25.2538
1.36 Dress Booth (xray room) | ___
1.37 OPD Clinic Pedia 1 | 14.3811
1.38 OPD Clinic Pedia 2 | 14.3811
1.39 OPD Records | 10.418 |  |  | 0.6
1.40 OPD info. And admitting | 9.9805
1.41 OPD Clinic Medical 1 | 14.4356
1.42 OPD Clinic Medical 2 | 14.4356
1.43 Hospital Main Lobby
1.44 Waste Disposal Area | 14.3639
1.45 X-RAY ROOM | ___
1.46 Pressing Area | 8.431
1.47 Linen Storage 1 | 8.3137
1.48 Linen Storage 2 | ___
1.49 Linen Office | 8.4375
1.50 Admin Office | 13.607
1.51 Male Toilet | 17.2599 | [7 empty] | 25
1.52 Waiting Area
1.53 Washing Area | 17.1267
1.54 Receiving Sorting Area | 8.5711
1.55 Administrative office | 35.3177
1.56 Social Welfare | 13.5984
1.57 Female Toilet | 17.0428 | [7 empty] | 25
1.58 OPD Info. And admitting | 10.4417
1.59 OPD records | 11.5919
1.60 Ultrasound | 19.0769 | 2.5344
1.61 Cooking Area | 34.2152
1.62 Dry storage | 2.5941
1.63 Cold Storage | 1.9625
1.64 Supply Receiving Area | 5.7184
1.65 Dietician's Office | 9.225 | 1.945
1.66 Dietary | 38.0325
1.67 Staff Dining | 50.8881
1.68 OPD clinic Ob-gyne | 27.0056 | 2.5344
1.69 Garbage Disposal area | 2.28
1.70 Canteen | 181.6992
Second Floor Plan
Name of Room | Base Area (m^2) | Base Area With Toilet | Outside Air req. (L/s-person) | Outside Air req. (L/m2) | Lighting used (W) | Lighting (W) | Equipments used | Eq. (W) | Temperature
5-Bed Ward 1 | 34.2769 |  | 13 | 25
5-Bed Ward 2 | 34.26 |  | 13 | 25
Waiting Area 1 | __ |  | __ | __
Waiting Area 2 | __ |  | __ | __
5-Bed Ward 3 | 34.29 |  | 13 | 25
5-Bed Ward 4 | 34.1175 |  | 13 | 25
Canopy
Isolation Room 1 | 13.6738 |  | 8 | 15
Private Room 1 | 13.9206 |  | 13 | 25
Private Room 2 | 13.8754 |  | 13 | 25
Chief Nurse | 30.712
Stretcher's Nook
Treatment Room | 17.9413 |  | 8 | 15
Nurse Station | 22.829
Dirty Utility | 4.7869
Clean Linen | 2.4581
Private Room 3 | 13.8735 |  | 13 | 25
Private Room 4 | 13.8928 |  | 13 | 25
Isolation Room 2 | 13.7066 |  | 8 | 15
Reception | 11.0522
Private Room 5 | 13.6813 |  | 13 | 25
Chief of Hospital | 18.7319
3-Bed Ward 1 | 25.372 |  | 13 | 25
Elevator
3-Bed Ward 2 | 25.48 |  | 13 | 25
Private Room 6 | 13.7512 |  | 13 | 25
Conference Room | 38.4537 |  | 2.5 | 0.3
3-Bed Ward 3 | 25.372 |  | 13 | 25
Waiting Area
3-Bed Ward 4 | 25.48 |  | 13 | 25
Private Room 7 | 13.7512 |  | 13 | 25
Private Room 8 | 13.7512 |  | 13 | 25
Canopy 2
Canopy 3
Chief of Clinics | 21.3616
CSSR | 31.4388
Delivery Room | 34.9862
Sub-Ster Room 1 | 5.4111
Labor Room | 25.7486
Pathologic Nursery | 16.7994
Pre-mature nursery | 16.7999
Breastfeeding room | 10.2258
Pre-operation area | 19.0007 |  | 8 | 15
Autoclave area | 14.9875
Sterile supply room | 21.6006
Work Area 1 | 23.6003 |  | 8 | 15
Canopy 4
Major Operating Room | 35.0425 |  | 15 | 30
Scrub-up area
Sub-Ster Room 2 | 5.6912
Jan.Clo. | 4.1338
Clean up room | 12.91
Nurse Station
Sterile instrument supply storage area | 7.4784
anesthesia office and storage | 17.5207
DR-1 | 2.8
DR-2 | 2.8
DR-3 | 2.8
Lounge Area
Recovery Room | 46.9742 |  | 8 | 15
Third Floor Plan
Name of Room | Base Area (m^2) | Base Area With Toilet | Outside Air req. (L/s-person) | Outside Air req. (L/m2) | Lighting used (W) | Lighting (W) | Equipments used | Eq. (W) | Temperature
5-Bed Ward 1 | 34.2769 | 2.6175 | 13 | 25
5-Bed Ward 2 | 34.26 | 2.6175 | 13 | 25
Waiting Area 1 | 37.4087
Waiting Area 2 | 37.4087
5-Bed Ward 3 | 34.26 | 2.6175 | 13 | 25
5-Bed Ward 4 | 34.26 | 2.6175 | 13 | 25
Canopy
Isolation Room 1 | 10.1393 | 2.6222 | 8 | 15
Private Room 1 | 13.9222 | 2.6155 | 13 | 25
Private Room 2 | 13.8738 | 2.6186 | 13 | 25
Chief Nurse | 30.712 | 2.6374
Stretcher's Nook | ___
Treatment Room | 17.9413 |  | 8 | 15
Nurse Station | 22.829 | 2.415
Dirty Utility | 4.7869
Clean Linen | 2.4581
Private Room 3 | 13.8735 | 2.6175 | 13 | 25
Private Room 4 | 13.8928 | 2.6175 | 13 | 25
Isolation Room 2 | 10.1716 | 2.6213 | 8 | 15
Private Room 5 | 15.8619 | 2.64 | 13 | 25
Privaate Room 6 | 15.8619 | 2.64 | 13 | 25
3-Bed Ward 1 | 24.783 | 2.64 | 13 | 25
3-Bed Ward 2 | 24.8909 | 2.64 | 13 | 25
Private Room 7 | 13.6813 | 2.64 | 13 | 25
Private Room 8 | 13.7512 | 2.64 | 13 | 25
Private Room 9 | 16.0112 | 2.64 | 13 | 25
Private Room 10 | 16.0112 | 2.64 | 13 | 25
Elevator | 8.9651
Private Room 11 | 13.7512 | 2.64 | 13 | 25
Private Room 12 | 13.7512 | 2.64 | 13 | 25
Waiting Area | 23.4829
Private Room 13 | 10.7572 | 2.64 | 13 | 25
Private Room 14 | 11.315 | 2.64 | 13 | 25
Solarium 1 | 13.3083
Stretcher's Wheelchair Nook 1 | 11.0872
Stretcher's Wheelchair Nook 2 | 8.275
Solarium 2 | 13.4675
Canopy 2
Water Tank 1 | 183.9438
Water Tank 2 | ___
Chapel | 58.8601
Male Toilet | 17.4452 | [7 empty] | 25
Female Toilet | 17.4806 | [7 empty] | 25
Waiting Area | 43.5914
Admitting | 10.9006
Billing | 10.7831
Cashier | 9.4163
Personel's dining | 26.9958 | 2.3994
computer room | [8 empty] | 21
dialysis | [8 empty] | 25
CT scanner | [8 empty] | 24
dining room | [8 empty] | 25
dry labs | [8 empty] | 25
elevator | [8 empty] | 36
examination room | [8 empty] | 24
icU | [8 empty] | 23~29
Isolation room | [8 empty] | 24
kitchen | [8 empty] | 27
laundry | [8 empty] | 28
locker room | [8 empty] | 25
londge | [8 empty] | 25
minor operating room | [8 empty] | 24
Office / conference room | [8 empty] | 25
operating room(60 to 80) | [8 empty] | 17~27
patient room | [8 empty] | 24
pharmacy | [8 empty] | 22
radiation therapy | [8 empty] | 24
recovery room | [8 empty] | 23
treatment room | [8 empty] | 24