## EXTERNAL WALL LOAD
EXTERNAL WALL LOAD
FIRST FLOOR
Space | Orientation | U | A(m^2) | CLTDsel | LM | k | Ti | Tave | CLTD adj | Q(W)
Power House | E | 2.7144 | 22 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 1492.92
Power House | N | 2.7144 | 16 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 564.5952
Maintenance Office | N | 2.7144 | 5.8 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 204.6658
Maintenance Office CR | N | 2.7144 | 5.04 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 177.8475
Female Toilet | N | 2.7144 | 11.28 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 398.0396
Male Toilet | N | 2.7144 | 11.28 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 398.0396
MINOR OPERATING ROOM | N | 2.7144 | 13.6 | 13 | 2.22 | 0.65 | 22 | 30.45 | 14.343 | 479.9059
Examination/Treatment AREA | N | 2.7144 | 19.6 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 691.6291
Examination/Treatment AREA | W | 2.7144 | 29.6 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 2651.4259
CR | N | 2.7144 | 8.08 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 285.1206
Cadaver Holding Room | E | 2.7144 | 22.4 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 1520.064
EMERGENCY ROOM | W | 2.7144 | 23.6 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 2113.9747
HALLWAY | W | 2.7144 | 49.85 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 4465.3237
Work Area (laboratory) | E | 2.7144 | 21.6 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 1465.776
WAITING AREA (CR) | E | 2.7144 | 6.12 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 415.3032
Film File Storage | E | 2.7144 | 6.04 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 409.8744
Pressing Area | E | 2.7144 | 10 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 678.6
Ultrasound | N | 2.7144 | 5.24 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 184.9049
Ultrasound | W | 2.7144 | 19.2 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 1719.8438
Ultrasound CR | N | 2.7144 | 6.4 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 225.8381
Ultrasound CR | W | 2.7144 | 7.04 | 33 | -0.55 | 0.65 | 24 | 30.45 | 23.5425 | 630.6094
Cooking Area | S | 2.7144 | 12.52 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 747.6543
Cooking Area | E | 2.7144 | 19.8 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 1343.628
Dietician's Office | S | 2.7144 | 11.6 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 692.7149
Dietician's Office CR | S | 2.7144 | 5.6 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 334.4141
Staff Dining | S | 2.7144 | 26.12 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 1559.8028
OPD clinic Ob-gyne | W | 2.7144 | 10.64 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 953.0801
OPD clinic Ob-gyne | S | 2.7144 | 19.4 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 1158.5059
CR | W | 2.7144 | 6.4 | 33 | -0.55 | 0.65 | 24 | 30.45 | 23.5425 | 573.2813
CR | S | 2.7144 | 6.84 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 408.4629
Canteen | W | 2.7144 | 39.2 | 33 | -0.55 | 0.65 | 24 | 30.45 | 23.5425 | 3511.3478
Canteen | E | 2.7144 | 44.8 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 3040.128
Canteen | S | 2.7144 | 50.8 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 3033.6134
Washing Area | E | 2.7144 | 10.27 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 696.9222
[9 empty] | Total Load: | 39227.8573
SECOND FLOOR
Space | Orientation | U | A(m^2) | CLTDsel | LM | k | Ti | Tave | CLTD adj | Q(W)
5 Bed Ward E | E | 2.7144 | 26 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 1400.3725
5 Bed Ward N | N | 2.7144 | 19.38 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 728.212
5 Bed Ward | N | 2.7144 | 19.38 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 728.212
Stairs N | N | 2.7144 | 43.2 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 1623.259
Stairs W | W | 2.7144 | 41.2 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 2800.5849
5-Bed Ward | N | 2.7144 | 19.38 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 728.212
5-Bed Ward N | N | 2.7144 | 19.38 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 728.212
5-Bed Ward W | W | 2.7144 | 26 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 1767.3594
Hallway (W) | W | 2.7144 | 9.7 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 659.361
Isolation room W | W | 2.7144 | 12.28 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 834.7374
Isolation room S | S | 2.7144 | 10.48 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 447.413
Isolation room CR | W | 2.7144 | 7.48 | 33 | -0.55 | 0.65 | 24 | 30.45 | 23.5425 | 478.0001
Private Room | W | 2.7144 | 9 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 611.7783
Private Room | W | 2.7144 | 9 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 611.7783
Private Room | W | 2.7144 | 9 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 611.7783
Private Room | W | 2.7144 | 9 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 611.7783
CSSR | W | 2.7144 | 13.05 | 33 | -0.55 | 0.65 | 24 | 30.45 | 23.5425 | 833.9441
Sterile Supply Room N | N | 2.7144 | 12 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 402.0461
Sterile Supply Room W | W | 2.7144 | 10.58 | 33 | -0.55 | 0.65 | 24 | 30.45 | 23.5425 | 676.1018
Recovery Room W | W | 2.7144 | 30.4 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 2066.451
Recovery Room S | S | 2.7144 | 21.6 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 922.149
Recovery Room CR | S | 2.7144 | 4.44 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 171.4749
Hallway (S) | S | 2.7144 | 19.2 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 819.688
Lounge Area | S | 2.7144 | 21.2 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 905.0722
DR-1 | S | 2.7144 | 5.04 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 215.1681
DR-2 | S | 2.7144 | 5.04 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 215.1681
DR-3 | S | 2.7144 | 5.04 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 215.1681
Anesthesia Off. And Storage | S | 2.7144 | 9.8 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 378.4807
Sterile Storage | S | 2.7144 | 8.8 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 339.8603
Clean-up Room | S | 2.7144 | 10.4 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 401.653
Sub-Ster Room | S | 2.7144 | 10.4 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 443.9977
Major Operating Room S | S | 2.7144 | 6 | 22 | -3.88 | 0.65 | 22 | 30.45 | 16.228 | 264.2957
Major Operating Room E | E | 2.7144 | 6 | 25 | -0.55 | 0.65 | 22 | 30.45 | 20.3425 | 331.3061
Fire Exit | E | 2.7144 | 8.6 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 463.2001
Delivery Room E | E | 2.7144 | 24 | 25 | -0.55 | 0.65 | 22 | 30.45 | 20.3425 | 1325.2244
Delivery Room N | N | 2.7144 | 9.4 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 353.2091
Chief of Clinics | E | 2.7144 | 12.9 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 694.8002
Conference Room | E | 2.7144 | 20.4 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 1098.7538
Chief of Hospital | E | 2.7144 | 8.16 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 439.5015
Reception (CR) | E | 2.7144 | 10.2 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 549.3769
Isolation Room S | S | 2.7144 | 12.28 | 22 | -0.55 | 0.65 | 22.5 | 30.45 | 17.8925 | 596.4077
Isolation Room E | E | 2.7144 | 8.88 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 478.2811
Isolation Room CR | E | 2.7144 | 7.84 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 422.2662
[9 empty] | Total Load: | 31394.0945
THIRD FLOOR
Space | Orientation | U | A(m^2) | CLTDsel | LM | k | Ti | Tave | CLTD adj | Q(W)
5 Bed Ward E | E | 2.7144 | 26 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 1764.36
5 Bed Ward N | N | 2.7144 | 19.4 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 684.5717
5 Bed Ward | N | 2.7144 | 19.4 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 684.5717
Stairs E | E | 2.7144 | 40.92 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 2776.8312
Stairs N | N | 2.7144 | 68 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 2399.5296
Stairs W | W | 2.7144 | 40.92 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 3665.4172
5 Bed Ward | N | 2.7144 | 19.4 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 684.5717
5 Bed Ward N | N | 2.7144 | 19.4 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 684.5717
5 Bed Ward W | W | 2.7144 | 26 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 2328.9552
Hallway | W | 2.7144 | 9.7 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 868.8794
Isolation Room W | W | 2.7144 | 13.4 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 1200.3077
Isolation Room CR | W | 2.7144 | 8.56 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 766.7637
Isolation Room S | S | 2.7144 | 12 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 716.6016
Private Room | W | 2.7144 | 10.6 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 949.4971
Private Room | W | 2.7144 | 10.6 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 949.4971
Private Room | W | 2.7144 | 10.6 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 949.4971
Private Room | W | 2.7144 | 10.6 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 949.4971
Solarium | W | 2.7144 | 11.65 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 1043.5511
Admitting N | N | 2.7144 | 12 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 423.4464
Admitting W | W | 2.7144 | 13.2 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 1182.3926
Billing | W | 2.7144 | 13.2 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 1182.3926
Cashier | W | 2.7144 | 10.4 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 931.5821
Personel's Dining W | W | 2.7144 | 7.69 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 688.8333
Personel's Dining CR W | W | 2.7144 | 7.16 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 641.3584
Personel's Dining CR S | S | 2.7144 | 5.64 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 336.8028
Personel's Dining S | S | 2.7144 | 20.4 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 1218.2227
Stairs S | S | 2.7144 | 19.2 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 1146.5626
Female Toilet | S | 2.7144 | 11.28 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 673.6055
Male Toilet | S | 2.7144 | 11.28 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 673.6055
Hallway S | S | 2.7144 | 24 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 1433.2032
Water Tank S | S | 2.7144 | 48 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 2866.4064
Water Tank E | E | 2.7144 | 61.6 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 4180.176
Water Tank N | N | 2.7144 | 8.88 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 313.3503
Solarium | E | 2.7144 | 11.67 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 791.9262
Private Room | E | 2.7144 | 10.6 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 719.316
Private Room | E | 2.7144 | 10.6 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 719.316
Private Room | E | 2.7144 | 10.6 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 719.316
Private Room | E | 2.7144 | 10.6 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 719.316
Isolation Room S | S | 2.7144 | 8.88 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 530.2852
Isolation Room E | E | 2.7144 | 13.4 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 909.324
Isolation Room CR | E | 2.7144 | 9.04 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 613.4544
Fire Exit | E | 2.7144 | 2.4 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 162.864
[9 empty] | Total Load | 47844.5301

## GLASS LOAD
GLASS LOAD
FIRST FLOOR
Space | Orientation | U | To | Ti | A(m^2) | SHGF | SCL | SC | Qsg (W) | Qth (W)
Power House | E | 2.8722 | 34.5 | 22.5 | 2 | 685 | 0.8 | 0.55 | 602.8 | 68.9328 | E=685 | 0.8
Maintenance Office | N | 2.8722 | 34.5 | 22.5 | 1.2 | 120 | 0.91 | 0.55 | 72.072 | 41.3597 | N=120 | 0.91
Maintenance Office CR | N | 2.8722 | 34.5 | 22.5 | 0.36 | 120 | 0.91 | 0.55 | 21.6216 | 12.4079 | W=685 | 0.82
Famale Toilet | N | 2.8722 | 34.5 | 24 | 0.72 | 120 | 0.91 | 0.55 | 43.2432 | 21.7138 | S=230 | 0.83
Male Toilet | N | 2.8722 | 34.5 | 24 | 0.72 | 120 | 0.91 | 0.55 | 43.2432 | 21.7138
Minor Operating Room | N | 2.8211 | 34.5 | 22 | 1.6 | 120 | 0.91 | 0.55 | 96.096 | 56.422
Exaination/Treatment and Obs Area | N | 2.8722 | 34.5 | 22.5 | 2.2 | 120 | 0.91 | 0.55 | 132.132 | 75.8261
Exaination/Treatment and Obs Area CR | N | 2.8722 | 34.5 | 22.5 | 0.72 | 120 | 0.91 | 0.55 | 43.2432 | 24.8158
Emergency Room | W | 2.8722 | 34.5 | 22.5 | 2 | 685 | 0.82 | 0.55 | 617.87 | 68.9328
Hallway | W | 2.8722 | 34.5 | 22.5 | 2.75 | 685 | 0.82 | 0.55 | 849.5712 | 94.7826
Hallway | W | 2.8211 | 34.5 | 22.5 | 9 | 685 | 0.82 | 0.55 | 2780.415 | 304.6788
Ultrasound N | N | 2.8722 | 34.5 | 22.5 | 0.6 | 120 | 0.91 | 0.55 | 36.036 | 20.6798
Ultrasound W | W | 2.8722 | 34.5 | 22.5 | 4.2 | 685 | 0.82 | 0.55 | 1297.527 | 144.7589
Ultrasound CR | W | 2.8722 | 34.5 | 24 | 0.36 | 685 | 0.82 | 0.55 | 111.2166 | 10.8569
OPB Clinic OB-Gyne W | W | 2.8722 | 34.5 | 22.5 | 0.6 | 685 | 0.82 | 0.55 | 185.361 | 20.6798
OPB Clinic OB-Gyne S | S | 2.8722 | 34.5 | 22.5 | 1.6 | 230 | 0.83 | 0.55 | 167.992 | 55.1462
OPB Clinic OB-Gyne CR | S | 2.8722 | 34.5 | 24 | 0.36 | 230 | 0.83 | 0.55 | 37.7982 | 10.8569
Canteen W | W | 2.8722 | 34.5 | 24 | 4.2 | 685 | 0.82 | 0.55 | 1297.527 | 126.664
Canteen S | S | 2.8722 | 34.5 | 24 | 8.4 | 230 | 0.83 | 0.55 | 881.958 | 253.328
Canteen E | E | 2.8722 | 34.5 | 24 | 1.4 | 685 | 0.8 | 0.55 | 421.96 | 42.2213
Dietary | S | 2.8722 | 34.5 | 22.5 | 2.4 | 230 | 0.83 | 0.55 | 251.988 | 82.7194
Dietitian Office | S | 2.8722 | 34.5 | 22.5 | 2.8 | 230 | 0.83 | 0.55 | 293.986 | 96.5059
Cooking Area S | S | 2.8722 | 34.5 | 24 | 1.8 | 230 | 0.83 | 0.55 | 188.991 | 54.2846
Cooking Area E | E | 2.8722 | 34.5 | 24 | 2.4 | 685 | 0.8 | 0.55 | 723.36 | 72.3794
Washing Area | E | 2.8722 | 34.5 | 24 | 1.73 | 685 | 0.8 | 0.55 | 521.422 | 52.1735
Pressing Area | E | 2.8722 | 34.5 | 22.5 | 2 | 685 | 0.8 | 0.55 | 602.8 | 68.9328
Film File Storage | E | 2.8722 | 34.5 | 22.5 | 0.36 | 685 | 0.8 | 0.55 | 108.504 | 12.4079
Waiting Area CR | E | 2.8722 | 34.5 | 24 | 0.36 | 685 | 0.8 | 0.55 | 108.504 | 10.8569
Work Area Laboratory | E | 2.8722 | 34.5 | 22.5 | 2.4 | 685 | 0.8 | 0.55 | 723.36 | 82.7194
Cadaver Holding Room | E | 2.8722 | 34.5 | 22.5 | 1.6 | 685 | 0.8 | 0.55 | 482.24 | 55.1462
[7 empty] | Total: |  | 13744.8383 | 2064.9042
[7 empty] | Overall Total Load: |  | 15809.7425
SECOND FLOOR
Space | Orientation | U | To | Ti | A(m^2) | SHGF | SCL | SC | Qsg (W) | Qth (W)
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 4.62 | 120 | 0.91 | 0.55 | 277.4772 | 159.2348
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 4.62 | 120 | 0.91 | 0.55 | 277.4772 | 159.2348 |  |  | Awning or Sliding | 2.8722
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 4.62 | 120 | 0.91 | 0.55 | 277.4772 | 159.2348 |  |  | Fixed | 2.8211
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 4.62 | 120 | 0.91 | 0.55 | 277.4772 | 159.2348
Hallway | W | 2.8211 | 34.5 | 22.5 | 2.7 | 685 | 0.82 | 0.55 | 834.1245 | 91.4036
Isolation Room | W | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.82 | 0.55 | 432.509 | 48.253
Isolation Room CR | W | 2.8722 | 34.5 | 24 | 0.36 | 685 | 0.82 | 0.55 | 111.2166 | 10.8569
Private Room | W | 2.8722 | 34.5 | 22.5 | 3 | 685 | 0.82 | 0.55 | 926.805 | 103.3992
Private Room | W | 2.8722 | 34.5 | 22.5 | 3 | 685 | 0.82 | 0.55 | 926.805 | 103.3992
Private Room | W | 2.8722 | 34.5 | 22.5 | 3 | 685 | 0.82 | 0.55 | 926.805 | 103.3992
Private Room | W | 2.8722 | 34.5 | 22.5 | 3 | 685 | 0.82 | 0.55 | 926.805 | 103.3992
CSSR | W | 2.8722 | 34.5 | 22.5 | 1.95 | 685 | 0.82 | 0.55 | 602.4232 | 67.2095
Sterile Supply Room | W | 2.8722 | 34.5 | 24 | 5.02 | 230 | 0.82 | 0.55 | 520.7246 | 151.3937
Recovery Room | S | 2.8722 | 34.5 | 22.5 | 2.4 | 230 | 0.83 | 0.55 | 251.988 | 82.7194
Recovery Room CR | S | 2.8722 | 34.5 | 24 | 0.36 | 230 | 0.83 | 0.55 | 37.7982 | 10.8569
Lounge Area | S | 2.8722 | 34.5 | 22.5 | 2.8 | 230 | 0.83 | 0.55 | 293.986 | 96.5059
DR 1 | S | 2.8722 | 34.5 | 22.5 | 0.36 | 230 | 0.83 | 0.55 | 37.7982 | 12.4079
DR 2 | S | 2.8722 | 34.5 | 22.5 | 0.36 | 230 | 0.83 | 0.55 | 37.7982 | 12.4079
DR 3 | S | 2.8722 | 34.5 | 22.5 | 0.36 | 230 | 0.83 | 0.55 | 37.7982 | 12.4079
Anesthesia Off. and Storage | S | 2.8722 | 34.5 | 24 | 1.6 | 230 | 0.83 | 0.55 | 167.992 | 48.253
Sterile Storage | S | 2.8722 | 34.5 | 24 | 1.6 | 230 | 0.83 | 0.55 | 167.992 | 48.253
Clean-up Room | S | 2.8722 | 34.5 | 24 | 1.6 | 230 | 0.83 | 0.55 | 167.992 | 48.253
Sub-Ster Room | S | 2.8722 | 34.5 | 22.5 | 1.6 | 230 | 0.83 | 0.55 | 167.992 | 55.1462
Chief of Clinics | E | 2.8722 | 34.5 | 22.5 | 2.1 | 685 | 0.8 | 0.55 | 632.94 | 72.3794
Conference Room | E | 2.8722 | 34.5 | 22.5 | 3.6 | 685 | 0.8 | 0.55 | 1085.04 | 124.079
Chief of Hospital | E | 2.8722 | 34.5 | 22.5 | 2.72 | 685 | 0.8 | 0.55 | 819.808 | 93.7486
Reception (CR) | S | 2.8722 | 34.5 | 22.5 | 1.2 | 230 | 0.83 | 0.55 | 125.994 | 41.3597
Isolation Room | E | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.8 | 0.55 | 421.96 | 48.253
Isolation Room CR | E | 2.8722 | 34.5 | 24 | 0.36 | 685 | 0.8 | 0.55 | 108.504 | 10.8569
[7 empty] | Total: |  | 11881.5076 | 2237.5402
[7 empty] | Overall Total Load |  | 14119.0478
THIRD FLOOR
Space | Orientation | U | To | Ti | A(m^2) | SHGF | SCL | SC | Qsg (W) | Qth (W)
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 2.31 | 120 | 0.91 | 0.55 | 138.7386 | 79.6174
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 2.31 | 120 | 0.91 | 0.55 | 138.7386 | 79.6174
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 2.31 | 120 | 0.91 | 0.55 | 138.7386 | 79.6174
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 2.31 | 120 | 0.91 | 0.55 | 138.7386 | 79.6174
Hallway | W | 2.8722 | 34.5 | 22.5 | 2.7 | 685 | 0.82 | 0.55 | 834.1245 | 93.0593
Isolation Room | W | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.82 | 0.55 | 432.509 | 48.253
Private Room | W | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.82 | 0.55 | 432.509 | 48.253
Private Room | W | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.82 | 0.55 | 432.509 | 48.253
Private Room | W | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.82 | 0.55 | 432.509 | 48.253
Private Room | W | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.82 | 0.55 | 432.509 | 48.253
Solarium | W | 2.8211 | 34.5 | 22.5 | 3.35 | 685 | 0.82 | 0.55 | 1034.9322 | 113.4082
Admitting | W | 2.8722 | 34.5 | 22.5 | 2.4 | 685 | 0.82 | 0.55 | 741.444 | 82.7194
Billing | W | 2.8722 | 34.5 | 22.5 | 2.4 | 685 | 0.82 | 0.55 | 741.444 | 82.7194
Cashier | W | 2.8722 | 34.5 | 22.5 | 2.4 | 685 | 0.82 | 0.55 | 741.444 | 82.7194
Personel's Dining W | W | 2.8722 | 34.5 | 22.5 | 2.23 | 685 | 0.82 | 0.55 | 688.925 | 76.8601
Personel's Dining CR | W | 2.8722 | 34.5 | 24 | 0.36 | 685 | 0.82 | 0.55 | 111.2166 | 10.8569
Personel's Dining S | S | 2.8722 | 34.5 | 22.5 | 2.4 | 230 | 0.83 | 0.55 | 251.988 | 82.7194
Female Toilet | S | 2.8722 | 34.5 | 24 | 0.72 | 230 | 0.83 | 0.55 | 75.5964 | 21.7138
Male Toilet | S | 2.8722 | 34.5 | 24 | 0.72 | 230 | 0.83 | 0.55 | 75.5964 | 21.7138
Hallway S | S | 2.8722 | 34.5 | 22.5 | 0 | 230 | 0.83 | 0.55 | 0 | 0
Solarium | E | 2.8211 | 34.5 | 22.5 | 3.35 | 685 | 0.8 | 0.55 | 1009.69 | 113.4082
Private Room | E | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.8 | 0.55 | 421.96 | 48.253
Private Room | E | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.8 | 0.55 | 421.96 | 48.253
Private Room | E | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.8 | 0.55 | 421.96 | 48.253
Private Room | E | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.8 | 0.55 | 421.96 | 48.253
Isolation Room | E | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.8 | 0.55 | 421.96 | 48.253
Isolation Room CR | E | 2.8722 | 34.5 | 24 | 0.36 | 685 | 0.8 | 0.55 | 108.504 | 10.8569
[7 empty] | Total: |  | 11242.2046 | 1593.7539
[7 empty] | Overall Total Load |  | 12835.9585

## INFILTRATION LOAD
INFILTRATION LOAD
SPACE | Volume | L/s | To | Ti | Wo | Wi | Qs (W) | Ql (W)
1.1 Power House | 149.7544 | 10.982 | 34.5 | 22.5 | 0.018137 | 0.0092932 | 162.3577 | 291.3582
1.2 Work Area | 38.6048 | 2.831 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 41.8538 | 82.0102
1.3 Storage Room | 31.27 | 2.2019 | 34.5 | 24 | 0.018137 | 0.0092932 | 28.4842 | 58.4184
1.4 Maintenance Office | 65.238 | 4.7841 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 70.7284 | 138.5884
1.4 Maintenance Office CR | 11.35 | 0.79923 | 34.5 | 24 | 0.018137 | 0.0092932 | 10.3388 | 21.204
1.5 Female toilet | 73.1964 | 5.1542 | 34.5 | 24 | 0.018137 | 0.0092932 | 66.6753 | 136.745
1.6 Male Toilet | 73.3856 | 5.1676 | 34.5 | 24 | 0.018137 | 0.0092932 | 66.8477 | 137.0985
1.7 Minor Operating Room | 93.5544 | 6.9516 | 34.5 | 22 | 0.018137 | 0.0082198 | 107.0548 | 206.8172
1.8 Equipment and supply storage area | 22.44 | 1.5802 | 34.5 | 24 | 0.018137 | 0.0092932 | 20.4408 | 41.9223
1.9 Examination/Treatment Area | 168.77 | 12.3765 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 182.9737 | 358.5268
1.9 Examination/Treatment Area CR | 14.8348 | 1.0446 | 34.5 | 24 | 0.018137 | 0.0092932 | 13.5132 | 27.7143
1.10 Cadaver Holding Room | 78.5512 | 5.7604 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 85.1621 | 166.8703
1.11 Supply Room | 125.1572 | 9.1782 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 135.6904 | 265.8779
1.12 Bulk Storage | 15.9088 | 1.1202 | 34.5 | 24 | 0.018137 | 0.0092932 | 14.4915 | 29.7207
1.13 Pharmacy | 82.9948 | 6.0863 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 89.9796 | 176.3101
1.14 Medical Records Office | 71.8048 | 5.2657 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 77.8479 | 152.5386
1.15 Medical Records | 74.5232 | 5.465 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 80.7951 | 158.3135
1.16 PHILHEALTH | 68.5512 | 5.0271 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 74.3205 | 145.6268
1.17 Doctor's Duty | 46.4248 | 3.4045 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 50.3319 | 98.6226
1.18 Nurse Station (ER) | 523.8728 | 38.4173 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 567.9619 | 1112.8898
1.18 Nurse Station (ER) CR | 11.9092 | 0.83861 | 34.5 | 24 | 0.018137 | 0.0092932 | 10.8482 | 22.2487
HALLWAY | 2624.716 | 192.4792 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 2845.6121 | 5575.8187
1.21 Work Area (laboratory) | 131.44 | 9.7667 | 34.5 | 22 | 0.018137 | 0.0082198 | 150.4075 | 290.5695
1.23 Waiting area | 50.71 | 3.7187 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 54.9778 | 107.7259
1.23 Waiting area CR | 12.9452 | 0.91156 | 34.5 | 24 | 0.018137 | 0.0092932 | 11.7919 | 24.1841
1.24 OPD clinic dental 1 | 57.5244 | 4.2185 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.3657 | 122.202
1.25 OPD clinic dental 2 | 57.5244 | 4.2185 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.3657 | 122.202
1.26 Elevator | 35.8604 | 2.6298 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 38.8784 | 76.1801
1.27 OPD clinic surgery 1 | 57.7424 | 4.2344 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.602 | 122.6651
1.28 OPD clinic surgery 2 | 57.7424 | 4.2344 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.602 | 122.6651
1.29 Cashier | 21.95 | 1.6097 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 23.7973 | 46.6295
1.30 Billing | 22.04 | 1.6163 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 23.8949 | 46.8207
1.31 Admitting | 22.5452 | 1.6533 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 24.4426 | 47.8939
1.32 Film File Storage | 22.0812 | 1.5549 | 34.5 | 24 | 0.018137 | 0.0092932 | 20.114 | 41.2519
1.33 Radiologist Office | 36.5968 | 2.6838 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 39.6768 | 77.7445
1.34 Dark Room | 19.8088 | 1.4526 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 21.4759 | 42.0808
1.35 Control Booth | 101.0152 | 7.4078 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 109.5166 | 214.5918
1.37 OPD Clinic Pedia 1 | 57.5244 | 4.2185 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.3657 | 122.202
1.38 OPD Clinic Pedia 2 | 57.5244 | 4.2185 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.3657 | 122.202
1.39 OPD Records | 41.672 | 3.0559 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 45.1791 | 88.526
1.40 OPD info. And admitting | 39.922 | 2.9276 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 43.2818 | 84.8084
1.41 OPD Clinic Medical 1 | 57.7424 | 4.2344 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.602 | 122.6651
1.42 OPD Clinic Medical 2 | 57.7424 | 4.2344 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.602 | 122.6651
1.44 Waste Disposal Area | 57.4556 | 4.2134 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.2911 | 122.0559
1.46 Pressing Area | 33.724 | 2.4731 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.5622 | 71.6416
1.47 Linen Storage | 33.2548 | 2.3417 | 34.5 | 24 | 0.018137 | 0.0092932 | 30.2921 | 62.1264
1.49 Linen Office | 33.75 | 2.475 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.5904 | 71.6969
1.50 Admin Office | 54.428 | 3.9914 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 59.0087 | 115.6242
1.51 Male Toilet | 69.0396 | 4.8615 | 34.5 | 24 | 0.018137 | 0.0092932 | 62.8889 | 128.9793
1.53 Washing Area | 68.5068 | 5.0238 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 74.2723 | 145.5325
1.54 Receiving Sorting Area | 34.2844 | 2.5142 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 37.1698 | 72.8321
1.55 Administrative office | 141.2708 | 10.3599 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 153.1602 | 300.1088
1.56 Social Welfare | 54.3936 | 3.9889 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 58.9714 | 115.5511
1.57 Female Toilet | 68.1712 | 4.8004 | 34.5 | 24 | 0.018137 | 0.0092932 | 62.0978 | 127.357
1.58 OPD Info. And admitting | 41.7668 | 3.0629 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 45.2819 | 88.7274
1.59 OPD records | 46.3676 | 3.4003 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 50.2699 | 98.5011
1.60 Ultrasound | 76.3076 | 5.5959 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 82.7296 | 162.1041
1.60 Ultrasound CR | 10.1376 | 0.71386 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.2344 | 18.939
1.61 Cooking Area | 136.8608 | 9.6373 | 34.5 | 24 | 0.018137 | 0.0092932 | 124.6679 | 255.6824
1.62 Dry storage | 10.3764 | 0.73067 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.452 | 19.3851
1.63 Cold Storage | 7.85 | 0.55277 | 34.5 | 24 | 0.018137 | 0.0092932 | 7.1506 | 14.6653
1.64 Supply Receiving Area | 22.8736 | 1.6774 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 24.7986 | 48.5916
1.65 Dietician's Office | 36.9 | 2.706 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 40.0055 | 78.3886
1.65 Dietician's Office CR | 7.78 | 0.54784 | 34.5 | 24 | 0.018137 | 0.0092932 | 7.0869 | 14.5345
1.66 Dietary | 152.13 | 11.1562 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 164.9333 | 323.1776
1.67 Staff Dining | 203.5524 | 14.9272 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 220.6834 | 432.4168
1.68 OPD clinic Ob-gyne | 108.0224 | 7.9216 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 117.1136 | 229.4775
1.68 OPD clinic Ob-gyne CR | 10.1376 | 0.71386 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.2344 | 18.939
1.69 Garbage Disposal area | 9.12 | 0.6688 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 9.8875 | 19.3741
1.70 Canteen | 726.7968 | 51.1786 | 34.5 | 24 | 0.018137 | 0.0092932 | 662.0465 | 1357.7967
[5 empty] | Total |  | 8169.4957 | 16087.9229
[5 empty] | Total Load |  | 24257.4187
SECOND FLOOR
SPACE | Volume | L/s | To | Ti | Wo | Wi | Qs (W) | Ql (W)
5-Bed Ward 1 | 137.1076 | 10.0546 | 34.5 | 22.5 | 0.018137 | #NAME? | 148.4053 | #NAME?
5-Bed Ward 1 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5217 | #NAME?
5-Bed Ward 2 | 137.04 | 10.0496 | 34.5 | 22.5 | 0.018137 | #NAME? | 148.3321 | #NAME?
5-Bed Ward 2 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5217 | #NAME?
Hallway 1 | 881.3296 | 64.6308 | 34.5 | 22.5 | 0.018137 | #NAME? | 953.9512 | #NAME?
Hallway 2 | 573.1645 | 42.0321 | 34.5 | 22.5 | 0.018137 | #NAME? | 620.3933 | #NAME?
Hallway 3 | 315.0296 | 23.1022 | 34.5 | 22.5 | 0.018137 | #NAME? | 340.988 | #NAME?
Hallway 4 | 398.6188 | 29.232 | 34.5 | 22.5 | 0.018137 | #NAME? | 431.465 | #NAME?
Hallway 5 | 571.5204 | 41.9115 | 34.5 | 22.5 | 0.018137 | #NAME? | 618.6137 | #NAME?
5-Bed Ward 3 | 137.16 | 10.0584 | 34.5 | 22.5 | 0.018137 | #NAME? | 148.462 | #NAME?
5-Bed Ward 3 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5217 | #NAME?
5-Bed Ward 4 | 136.47 | 10.0078 | 34.5 | 22.5 | 0.018137 | #NAME? | 147.7151 | #NAME?
5-Bed Ward 4 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5217 | #NAME?
Isolation Room 1 | 54.6952 | 4.011 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.2021 | #NAME?
Isolation Room 1 CR | 10.4924 | 0.73884 | 34.5 | 24 | 0.018137 | #NAME? | 9.5421 | #NAME?
Private Room 1 | 55.6824 | 4.0834 | 34.5 | 22.5 | 0.018137 | #NAME? | 60.2706 | #NAME?
Private Room 1 CR | 10.462 | 0.7367 | 34.5 | 24 | 0.018137 | #NAME? | 9.5145 | #NAME?
Private Room 2 | 55.5016 | 4.0701 | 34.5 | 22.5 | 0.018137 | #NAME? | 60.0749 | #NAME?
Private Room 2 CR | 10.4788 | 0.73788 | 34.5 | 24 | 0.018137 | #NAME? | 9.5297 | #NAME?
Chief Nurse | 122.848 | 9.0089 | 34.5 | 22.5 | 0.018137 | #NAME? | 132.9707 | #NAME?
Chief Nurse CR | 10.5496 | 0.74287 | 34.5 | 24 | 0.018137 | #NAME? | 9.5941 | #NAME?
Treatment Room | 71.7652 | 5.2628 | 34.5 | 22.5 | 0.018137 | #NAME? | 77.6787 | #NAME?
Nurse Station | 91.316 | 6.6965 | 34.5 | 22.5 | 0.018137 | #NAME? | 98.8404 | #NAME?
Nurse Station CR | 9.6484 | 0.67941 | 34.5 | 24 | 0.018137 | #NAME? | 8.7746 | #NAME?
Dirty Utility | 19.1476 | 1.3483 | 34.5 | 24 | 0.018137 | #NAME? | 17.4134 | #NAME?
Clean Linen | 9.8324 | 0.69236 | 34.5 | 24 | 0.018137 | #NAME? | 8.9419 | #NAME?
Private Room 3 | 55.494 | 4.0696 | 34.5 | 22.5 | 0.018137 | #NAME? | 60.0667 | #NAME?
Private Room 3 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5217 | #NAME?
Private Room 4 | 55.5712 | 4.0752 | 34.5 | 22.5 | 0.018137 | #NAME? | 60.1503 | #NAME?
Private Room 4 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5217 | #NAME?
Isolation Room 2 | 54.8264 | 4.0206 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.3441 | #NAME?
Isolation Room 2 CR | 10.4852 | 0.73833 | 34.5 | 24 | 0.018137 | #NAME? | 9.5356 | #NAME?
Reception | 44.2088 | 3.242 | 34.5 | 22.5 | 0.018137 | #NAME? | 47.8516 | #NAME?
Private Room 5 | 54.7252 | 4.0132 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.2346 | #NAME?
Private Room 5 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6036 | #NAME?
Chief of Hospital | 74.9276 | 5.4947 | 34.5 | 22.5 | 0.018137 | #NAME? | 81.1016 | #NAME?
Chief of Hospital CR | 27.7184 | 1.9518 | 34.5 | 24 | 0.018137 | #NAME? | 25.208 | #NAME?
3-Bed Ward 1 | 101.488 | 7.4425 | 34.5 | 22.5 | 0.018137 | #NAME? | 109.8506 | #NAME?
3-Bed Ward 1 CR | 10.4348 | 0.73478 | 34.5 | 24 | 0.018137 | #NAME? | 9.4897 | #NAME?
Elevator | 26.4604 | 1.9404 | 34.5 | 22.5 | 0.018137 | #NAME? | 28.6407 | #NAME?
3-Bed Ward 2 | 101.92 | 7.4741 | 34.5 | 22.5 | 0.018137 | #NAME? | 110.3182 | #NAME?
3-Bed Ward 2 CR | 10.4348 | 0.73478 | 34.5 | 24 | 0.018137 | #NAME? | 9.4897 | #NAME?
Private Room 6 | 55.0048 | 4.0337 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.5372 | #NAME?
Private Room 6 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6036 | #NAME?
Conference Room | 153.8148 | 11.2798 | 34.5 | 22.5 | 0.018137 | #NAME? | 166.4891 | #NAME?
3-Bed Ward 3 | 101.488 | 7.4425 | 34.5 | 22.5 | 0.018137 | #NAME? | 109.8506 | #NAME?
3-Bed Ward 3 CR | 10.4348 | 0.73478 | 34.5 | 24 | 0.018137 | #NAME? | 9.4897 | #NAME?
3-Bed Ward 4 | 101.92 | 7.4741 | 34.5 | 22.5 | 0.018137 | #NAME? | 110.3182 | #NAME?
3-Bed Ward 4 CR | 10.4348 | 0.73478 | 34.5 | 24 | 0.018137 | #NAME? | 9.4897 | #NAME?
Private Room 7 | 55.0048 | 4.0337 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.5372 | #NAME?
Private Room 7 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6036 | #NAME?
Private Room 8 | 55.0048 | 4.0337 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.5372 | #NAME?
Private Room 8 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6036 | #NAME?
Chief of Clinics | 85.4464 | 6.2661 | 34.5 | 22.5 | 0.018137 | #NAME? | 92.4872 | #NAME?
Chief of Clinics CR | 6.6584 | 0.46886 | 34.5 | 24 | 0.018137 | #NAME? | 6.0554 | #NAME?
CSSR | 125.7552 | 9.222 | 34.5 | 22.5 | 0.018137 | #NAME? | 136.1174 | #NAME?
Delivery Room | 139.9448 | 10.3987 | 34.5 | 22 | 0.018137 | #NAME? | 159.8796 | #NAME?
Sub-Ster Room 1 | 21.6444 | 1.5241 | 34.5 | 24 | 0.018137 | #NAME? | 19.6841 | #NAME?
Labor Room | 102.9944 | 7.5529 | 34.5 | 22.5 | 0.018137 | #NAME? | 111.4811 | #NAME?
Labor Room CR | 15.452 | 1.0881 | 34.5 | 24 | 0.018137 | #NAME? | 14.0525 | #NAME?
Pathologic Nursery | 67.1976 | 4.9278 | 34.5 | 22.5 | 0.018137 | #NAME? | 72.7347 | #NAME?
Pre-mature nursery | 67.1996 | 4.928 | 34.5 | 22.5 | 0.018137 | #NAME? | 72.7368 | #NAME?
Breastfeeding room | 40.9032 | 2.9996 | 34.5 | 22.5 | 0.018137 | #NAME? | 44.2736 | #NAME?
Pre-operation area | 76.0028 | 5.6474 | 34.5 | 22 | 0.018137 | #NAME? | 86.8292 | #NAME?
Autoclave area | 59.95 | 4.3963 | 34.5 | 22.5 | 0.018137 | #NAME? | 64.8899 | #NAME?
Autoclave area CR | 6.72 | 0.4732 | 34.5 | 24 | 0.018137 | #NAME? | 6.1114 | #NAME?
Sterile supply room | 86.4024 | 6.0842 | 34.5 | 24 | 0.018137 | #NAME? | 78.577 | #NAME?
Work Area 1 | 94.4012 | 6.9228 | 34.5 | 22.5 | 0.018137 | #NAME? | 102.1799 | #NAME?
Major Operating Room | 140.17 | 10.4154 | 34.5 | 22 | 0.018137 | #NAME? | 160.1369 | #NAME?
Sub-Ster Room 2 | 22.7648 | 1.603 | 34.5 | 24 | 0.018137 | #NAME? | 20.703 | #NAME?
Jan.Clo. | 16.5352 | 1.1644 | 34.5 | 24 | 0.018137 | #NAME? | 15.0376 | #NAME?
Clean up room | 51.64 | 3.6363 | 34.5 | 24 | 0.018137 | #NAME? | 46.963 | #NAME?
Sterile Instrument Supply Storage Area | 29.9136 | 2.1064 | 34.5 | 24 | 0.018137 | #NAME? | 27.2044 | #NAME?
Anesthesia Office & Storage | 70.0828 | 4.935 | 34.5 | 24 | 0.018137 | #NAME? | 63.7355 | #NAME?
DR-1 | 11.2 | 0.78867 | 34.5 | 24 | 0.018137 | #NAME? | 10.1856 | #NAME?
DR-2 | 11.2 | 0.78867 | 34.5 | 24 | 0.018137 | #NAME? | 10.1856 | #NAME?
DR-3 | 11.2 | 0.78867 | 34.5 | 24 | 0.018137 | #NAME? | 10.1856 | #NAME?
Lounge Area | 165.2084 | 12.1153 | 34.5 | 22.5 | 0.018137 | #NAME? | 178.8216 | #NAME?
Recovery Room | 187.8968 | 13.7791 | 34.5 | 22.5 | 0.018137 | #NAME? | 203.3795 | #NAME?
Recovery Room CR | 8.3604 | 0.58871 | 34.5 | 24 | 0.018137 | #NAME? | 7.6032 | #NAME?
[5 empty] | Total: |  | 7292.9802 | #NAME?
[5 empty] | Overall Total Load |  | #NAME?
Space | Volume | L/s | To | Ti | Wo | Wi | Qs | Ql
5-Bed Ward 1 | 137.1076 | 10.0546 | 34.5 | 22.5 | 0.018137 | #NAME? | 148.6466 | #NAME?
5-Bed Ward 1 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5372 | #NAME?
5-Bed Ward 2 | 137.04 | 10.0496 | 34.5 | 22.5 | 0.018137 | #NAME? | 148.5733 | #NAME?
5-Bed Ward 2 CR | 10.47 | 0.7678 | 34.5 | 22.5 | 0.018137 | #NAME? | 11.3512 | #NAME?
Waiting Area 1 | 149.6348 | 10.9732 | 34.5 | 22.5 | 0.018137 | #NAME? | 162.2281 | #NAME?
Waiting Area 2 | 149.6348 | 10.9732 | 34.5 | 22.5 | 0.018137 | #NAME? | 162.2281 | #NAME?
5-Bed Ward 3 | 137.04 | 10.0496 | 34.5 | 22.5 | 0.018137 | #NAME? | 148.5733 | #NAME?
5-Bed Ward 3 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5372 | #NAME?
5-Bed Ward 4 | 137.04 | 10.0496 | 34.5 | 22.5 | 0.018137 | #NAME? | 148.5733 | #NAME?
5-Bed Ward 4 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5372 | #NAME?
Isolation Room 1 | 40.5572 | 2.9742 | 34.5 | 22.5 | 0.018137 | #NAME? | 43.9705 | #NAME?
Isolation Room 1 CR | 10.4888 | 0.73859 | 34.5 | 24 | 0.018137 | #NAME? | 9.5544 | #NAME?
Private Room 1 | 55.6888 | 4.0838 | 34.5 | 22.5 | 0.018137 | #NAME? | 60.3756 | #NAME?
Private Room 1 CR | 10.462 | 0.7367 | 34.5 | 24 | 0.018137 | #NAME? | 9.5299 | #NAME?
Private Room 2 | 55.4952 | 4.0696 | 34.5 | 22.5 | 0.018137 | #NAME? | 60.1657 | #NAME?
Private Room 2 CR | 10.4744 | 0.73757 | 34.5 | 24 | 0.018137 | #NAME? | 9.5412 | #NAME?
Chief Nurse | 122.848 | 9.0089 | 34.5 | 22.5 | 0.018137 | #NAME? | 133.1869 | #NAME?
Chief Nurse CR | 10.5496 | 0.74287 | 34.5 | 24 | 0.018137 | #NAME? | 9.6097 | #NAME?
Treatment Room | 71.7652 | 5.2628 | 34.5 | 22.5 | 0.018137 | #NAME? | 77.805 | #NAME?
Nurse Station | 91.316 | 6.6965 | 34.5 | 22.5 | 0.018137 | #NAME? | 99.0012 | #NAME?
Nurse Station CR | 9.66 | 0.68022 | 34.5 | 24 | 0.018137 | #NAME? | 8.7994 | #NAME?
Dirty Utility | 19.1476 | 1.3483 | 34.5 | 24 | 0.018137 | #NAME? | 17.4417 | #NAME?
Clean Linen | 9.8324 | 0.69236 | 34.5 | 24 | 0.018137 | #NAME? | 8.9564 | #NAME?
Private Room 3 | 55.494 | 4.0696 | 34.5 | 22.5 | 0.018137 | #NAME? | 60.1644 | #NAME?
Private Room 3 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5372 | #NAME?
Private Room 4 | 55.5712 | 4.0752 | 34.5 | 22.5 | 0.018137 | #NAME? | 60.2481 | #NAME?
Private Room 4 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | #NAME? | 9.5372 | #NAME?
Isolation Room 2 | 40.6864 | 2.9837 | 34.5 | 22.5 | 0.018137 | #NAME? | 44.1106 | #NAME?
Isolation Room 2 CR | 10.4852 | 0.73833 | 34.5 | 24 | 0.018137 | #NAME? | 9.5511 | #NAME?
Private Room 5 | 63.4476 | 4.6528 | 34.5 | 22.5 | 0.018137 | #NAME? | 68.7874 | #NAME?
Private Room 5 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Private Room 6 | 63.4476 | 4.6528 | 34.5 | 22.5 | 0.018137 | #NAME? | 68.7874 | #NAME?
Private Room 6 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
3-Bed Ward 1 | 99.132 | 7.2697 | 34.5 | 22.5 | 0.018137 | #NAME? | 107.4749 | #NAME?
3-Bed Ward 1 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
3-Bed Ward 2 | 99.5636 | 7.3013 | 34.5 | 22.5 | 0.018137 | #NAME? | 107.9429 | #NAME?
3-Bed Ward 2 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Private Room 7 | 54.7252 | 4.0132 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.3309 | #NAME?
Private Room 7 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Private Room 8 | 55.0048 | 4.0337 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.634 | #NAME?
Private Room 8 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Private Room 9 | 64.0448 | 4.6966 | 34.5 | 22.5 | 0.018137 | #NAME? | 69.4348 | #NAME?
Private Room 9 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Private Room 10 | 64.0448 | 4.6966 | 34.5 | 22.5 | 0.018137 | #NAME? | 69.4348 | #NAME?
Private Room 10 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Elevator | 35.8604 | 2.6298 | 34.5 | 22.5 | 0.018137 | #NAME? | 38.8784 | #NAME?
Private Room 11 | 55.0048 | 4.0337 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.634 | #NAME?
Private Room 11 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Private Room 12 | 55.0048 | 4.0337 | 34.5 | 22.5 | 0.018137 | #NAME? | 59.634 | #NAME?
Private Room 12 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Waiting Area | 93.9316 | 6.8883 | 34.5 | 22.5 | 0.018137 | #NAME? | 101.8369 | #NAME?
Private Room 13 | 43.0288 | 3.1554 | 34.5 | 22.5 | 0.018137 | #NAME? | 46.6501 | #NAME?
Private Room 13 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Private Room 14 | 45.26 | 3.3191 | 34.5 | 22.5 | 0.018137 | #NAME? | 49.0691 | #NAME?
Private Room 14 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
Solarium 1 | 53.2332 | 3.9038 | 34.5 | 22.5 | 0.018137 | #NAME? | 57.7133 | #NAME?
Stretcher's Wheelchair Nook 1 | 44.3488 | 3.2522 | 34.5 | 22.5 | 0.018137 | #NAME? | 48.0812 | #NAME?
Stretcher's Wheelchair Nook 2 | 33.1 | 2.4273 | 34.5 | 22.5 | 0.018137 | #NAME? | 35.8857 | #NAME?
Solarium 2 | 53.87 | 3.9505 | 34.5 | 22.5 | 0.018137 | #NAME? | 58.4037 | #NAME?
Water Tank 1 and 2 | 735.7752 | 53.9568 | 34.5 | 22.5 | 0.018137 | #NAME? | 797.698 | #NAME?
Chapel | 235.4404 | 17.2656 | 34.5 | 22.5 | 0.018137 | #NAME? | 255.2551 | #NAME?
Male Toilet | 69.7808 | 4.9137 | 34.5 | 24 | 0.018137 | #NAME? | 63.564 | #NAME?
Female Toilet | 69.9224 | 4.9237 | 34.5 | 24 | 0.018137 | #NAME? | 63.693 | #NAME?
Waiting Area | 174.3656 | 12.7868 | 34.5 | 22.5 | 0.018137 | #NAME? | 189.0402 | #NAME?
Admitting | 43.6024 | 3.1975 | 34.5 | 22.5 | 0.018137 | #NAME? | 47.272 | #NAME?
Billing | 43.1324 | 3.163 | 34.5 | 22.5 | 0.018137 | #NAME? | 46.7624 | #NAME?
Cashier | 37.6652 | 2.7621 | 34.5 | 22.5 | 0.018137 | #NAME? | 40.8351 | #NAME?
Personel's dining | 107.9832 | 7.9188 | 34.5 | 22.5 | 0.018137 | #NAME? | 117.0711 | #NAME?
Personel's dining CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | #NAME? | 9.6192 | #NAME?
HALLWAY | 2512.0732 | 184.2187 | 34.5 | 22.5 | 0.018137 | #NAME? | 2723.4893 | #NAME?
[5 empty] | Total |  | 7336.2148 | #NAME?
[5 empty] | Total Load |  | #NAME?

## MISCELLANEOUS LOAD
GROUND FLOOR
SPACE | Equipment | WATTAGE | Cs | Cl | CLF | Qs (W) | Ql (W)
Maintenance office | CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 70.8 | 0.33 | 0.16 | 0.96 | 22.4294 | 11.328
Minor operating room | SMOKE DETECTOR, 0.4W CARDIOPULMONARY BYPASS MACHINE, 150 W SURGICAL LGHTS, 25W AUTOCLAVE, 2000W ELECTROSURGERY, 109 W | 2284.4 | 0.33 | 0.16 | 0.96 | 723.6979 | 365.504
Examination/Treament Area | CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 70.8 | 0.33 | 0.16 | 0.96 | 22.4294 | 11.328
Supply Room | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Pharmacy | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Medical records office | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Philhealth | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Doctors on duty | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Emergency room | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Patho. office | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Radiologist office | TV, 125W TELEPHONE, 5W SMOKE DETECTOR, 1.6W CEILING ORBITAL FAN, 70W | 201.6 | 0.33 | 0.16 | 0.96 | 63.8669 | 32.256
X-ray Room | X-RAY MACHINE, 1500W SMOKE DETECTOR, 0.8W | 1500.8 | 0.33 | 0.16 | 0.96 | 475.4534 | 240.128
OPD Clinic Dental 1 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic Dental 2 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic surgery 1 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic surgery 1 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic Pedia 1 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic Pedia 2 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic Medical 1 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic Medical 2 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD info and admitting 1 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD ob-gyne | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Cashier | TV, 125W TELEPHONE, 5W CASH REGISTER, 100W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 525.8 | 0.33 | 0.16 | 0.96 | 166.5734 | 84.128
Billing | TV, 125W TELEPHONE, 5W CASH REGISTER, 100W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 525.8 | 0.33 | 0.16 | 0.96 | 166.5734 | 84.128
Admitting | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Administrative Office | TELEPHONE, 5W TV, 125W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 425.8 | 0.33 | 0.16 | 0.96 | 134.8934 | 68.128
Admin Office | TELEPHONE, 5W TV, 125W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 425.8 | 0.33 | 0.16 | 0.96 | 134.8934 | 68.128
Social Welfare | TELEPHONE, 5W TV, 125W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 425.8 | 0.33 | 0.16 | 0.96 | 134.8934 | 68.128
OPD info and admitting 2 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Ultrasound | TV, 150W TELEPHONE, 5W ULTRASOUND MACHINE, 95W SMOKE DETECTOR, 0.4W | 250.4 | 0.33 | 0.16 | 0.96 | 79.3267 | 40.064
OPD ob-gyne | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Canteen | TV, 150W TELEPHONE, 5W SMOKE DETECTOR, 1.2W CEILING ORBITAL FAN, 70W EXHAUST FAN, 40W | 266.2 | 0.33 | 0.16 | 0.96 | 84.3322 | 42.592
Dietitians office | TV, 150W TELEPHONE, 5W SMOKE DETECTOR, 0.4W | 155.4 | 0.33 | 0.16 | 0.96 | 49.2307 | 24.864
dry storage | SMOKE DETECTOR, 0.4W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
cold storage | SMOKE DETECTOR, 0.4W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Supply recieving area | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Cadaver Holding Room | SMOKE DETECTOR, 0.4W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Nurse Station | TV, 125 W TELEPHONE, 5 W COMPUTER, 225 W | 355 | 0.33 | 0.16 | 0.96 | 112.464 | 56.8
Hallway | SMOKE DETECTOR, 0.8W SPEAKER, 4W FIRE ALARM, 1 W CCTV(14), 56W | 61.8 | 0.33 | 0.16 | 0.96 | 19.5782 | 9.888
Cooking Area | OVEN, 1200 W REFRIGERATOR, 780W WATER DISPENSER, 600W | 2580 | 0.33 | 0.16 | 0.96 | 817.344 | 412.8
Staff Dining | SMOKE DETECTOR, 0.4W FRIDGE, 150W WATER DISPENSER, 600W | 750.4 | 0.33 | 0.16 | 0.96 | 237.7267 | 120.064
|  |  |  | Total |  | 5447.2493 | 2751.136
|  |  |  | Total Load |  | 8198.3853
SECOND FLOOR PLAN
SPACE | Equipment | Wattage | CS | Cl | CLF | Qs (W) | Ql (W)
5- Bed Ward 1 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
5- Bed Ward 2 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
5- Bed Ward 3 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
5- Bed Ward 4 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
Isolation Room | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W WALL FAN,25 W | 5.4 | 0.33 | 0.16 | 0.96 | 1.7107 | 0.864
Private Room 1 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 2 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 3 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 4 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 5 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 6 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 7 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 8 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Isolation Room 2 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W | 5.4 | 0.33 | 0.16 | 0.96 | 1.7107 | 0.864
Chief Nurse | SMOKE DETECTOR, 0.4W TELEPHONE, 5W COMPUTER, 225W | 230.4 | 0.33 | 0.16 | 0.96 | 72.9907 | 36.864
Treatment Room | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 70.4 | 0.33 | 0.16 | 0.96 | 22.3027 | 11.264
Nurse Station | TV, 125 W TELEPHONE, 5 W COMPUTER, 225 W | 355 | 0.33 | 0.16 | 0.96 | 112.464 | 56.8
Reception | SMOKE DETECTOR, 0.4W TELEPHONE, 5W | 5.4 | 0.33 | 0.16 | 0.96 | 1.7107 | 0.864
Chief of Hospital | TELEPHONE, 5W TV, 125W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 425.8 | 0.33 | 0.16 | 0.96 | 134.8934 | 68.128
Conference Room | TELEPHONE, 5W TV, 125W COMPUTER, 225W WATER DISPENSER, 600 W SMOKE DETECTOR, 0.8 W | 955.8 | 0.33 | 0.16 | 0.96 | 302.7974 | 152.928
Chief of Clinics | TELEPHONE, 5W TV, 125W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 425.8 | 0.33 | 0.16 | 0.96 | 134.8934 | 68.128
3-Bed Ward 1 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
3-Bed Ward 2 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
3-Bed Ward 3 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
3-Bed Ward 4 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
Delivery Room | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Labor Room | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Pathologic Nursery | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Pre-Mature Nursery | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
BreastFeeding Room | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Pre-operation Area | SMOKE DETECTOR, 0.4W CARDIOPULMONARY BYPASS MACHINE, 150 W SURGICAL LGHTS, 25W AUTOCLAVE, 2000W | 2175.4 | 0.33 | 0.16 | 0.96 | 689.1667 | 348.064
Autoclave Area | AUTOCLAVE, 1400 W SMOKE DETECTOR, 0.4 W | 1400.4 | 0.33 | 0.16 | 0.96 | 443.6467 | 224.064
Sterile Supply Room | TELEPHONE, 15W SMOKE DETECTOR, 0.4 W FRIDGE, 200 W | 215.4 | 0.33 | 0.16 | 0.96 | 68.2387 | 34.464
Recovery Room | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Lounge Area | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Anesthesia Office | SMOKE DETECTOR 0.4 W TELEPHONE, 5 W COMPUTER, 225 W ANESTHESIA SYSTEM, 166 W | 396.4 | 0.33 | 0.16 | 0.96 | 125.5795 | 63.424
Nurse Station | TV, 125 W TELEPHONE, 5 W COMPUTER, 225 W | 355 | 0.33 | 0.16 | 0.96 | 112.464 | 56.8
Major Operating Room | SMOKE DETECTOR, 0.4 W CARDIOPULMONARY BYPASS MACHINE, 150 W SURGICAL LGHTS, 25W VACUUM SUCTION, 302 W AUTOCLAVE, 2000W | 2477.4 | 0.33 | 0.16 | 0.96 | 784.8403 | 396.384
Clean Up Room | SMOKE DETECTOR, 0.4W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Hallway | SMOKE DETECTOR, 0.8W SPEAKER, 4W FIRE ALARM 1 W CCTV (10), 40 W | 45.8 | 0.33 | 0.16 | 0.96 | 14.5094 | 7.328
|  |  |  | Total |  | 3484.8253 | 1760.0128
|  |  |  | Total Load |  | 5244.8381
THIRD FLOOR PLAN
SPACE | Equipment | Wattage | Cs | Cl | CLF | Qs (W) | Qw (W)
5- Bed Ward 1 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
5- Bed Ward 2 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
5- Bed Ward 3 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
5- Bed Ward 4 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
Isolation Room | SMOKE DETECTOR, 0.4W TELEPHONE, 5W WALL FAN, 25W TV, 150 W | 175.9 | 0.33 | 0.16 | 0.96 | 55.7251 | 28.144
Private Room 1 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 2 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 3 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 4 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 5 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 6 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 7 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 8 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 9 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 10 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 11 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 12 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 13 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 14 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 15 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 16 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Chief Nurse | SMOKE DETECTOR, 0.4W TELEPHONE, 5W COMPUTER, 225W | 230.4 | 0.33 | 0.16 | 0.96 | 72.9907 | 36.864
Treatment Room | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 70.4 | 0.33 | 0.16 | 0.96 | 22.3027 | 11.264
Nurse Station | TV, 125 W TELEPHONE, 5 W COMPUTER, 225 W | 355 | 0.33 | 0.16 | 0.96 | 112.464 | 56.8
3-Bed Ward 1 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
3-Bed Ward 2 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
Admitting | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Billing | TV, 125W TELEPHONE, 5W CASH REGISTER, 100W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 525.8 | 0.33 | 0.16 | 0.96 | 166.5734 | 84.128
Cashier | TV, 125W TELEPHONE, 5W CASH REGISTER, 100W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 525.8 | 0.33 | 0.16 | 0.96 | 166.5734 | 84.128
Personel's Dining | SMOKE DETECTOR, 0.4W Fridge, 150W WATER, DISPENSER 600W Oven 1200W | 1950.4 | 0.33 | 0.16 | 0.96 | 617.8867 | 312.064
Chapel | HEAT DETECTOR, 0.16 W CEILING ORBITAL FAN, 50 W | 50.16 | 0.33 | 0.16 | 0.96 | 15.8907 | 8.0256
Solarium | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
Hallway | SMOKE DETECTOR, 0.8W SPEAKER, 4W FIRE ALARM,1W CCTV (10), 40W | 45.8 | 0.33 | 0.16 | 0.96 | 14.5094 | 7.328
|  |  |  | Total |  | 2187.5737 | 1104.8352
|  |  |  | Total Load |  | 3292.4089

## ROOF LOAD
THIRD FLOOR
TYPE 6, roof without suspended ceiling
SPACE | U | Area (m2) | CLTDmax | Ti | Tave | CLTDadj | Q(W)
5-Bed Ward 1 | 2.5844 | 34.2769 | 18 | 22.5 | 30.45 | 13.0875 | 1159.3501
5-Bed Ward 2 | 2.5844 | 34.26 | 18 | 22.5 | 30.45 | 13.0875 | 1158.7785
Waiting Area 1 | 2.5844 | 37.4087 | 18 | 22.5 | 30.45 | 13.0875 | 1265.2772
Waiting Area 2 | 2.5844 | 37.4087 | 18 | 22.5 | 30.45 | 13.0875 | 1265.2772
5-Bed Ward 3 | 2.5844 | 34.26 | 18 | 22.5 | 30.45 | 13.0875 | 1158.7785
5-Bed Ward 4 | 2.5844 | 34.26 | 18 | 22.5 | 30.45 | 13.0875 | 1158.7785
Isolation Room 1 | 2.5844 | 10.1393 | 18 | 22.5 | 30.45 | 13.0875 | 342.9423
Private Room 1 | 2.5844 | 13.9222 | 18 | 22.5 | 30.45 | 13.0875 | 470.8916
Private Room 2 | 2.5844 | 13.8738 | 18 | 22.5 | 30.45 | 13.0875 | 469.2546
Chief Nurse | 2.5844 | 30.712 | 18 | 22.5 | 30.45 | 13.0875 | 1038.7742
Treatment Room | 2.5844 | 17.9413 | 18 | 22.5 | 30.45 | 13.0875 | 606.8299
Nurse Station | 2.5844 | 22.829 | 18 | 22.5 | 30.45 | 13.0875 | 772.1469
Dirty Utility | 2.5844 | 4.7869 | 18 | 24 | 30.45 | 11.9625 | 147.9901
Clean Linen | 2.5844 | 2.4581 | 18 | 24 | 30.45 | 11.9625 | 75.9937
Private Room 3 | 2.5844 | 13.8735 | 18 | 22.5 | 30.45 | 13.0875 | 469.2444
Private Room 4 | 2.5844 | 13.8928 | 18 | 22.5 | 30.45 | 13.0875 | 469.8972
Isolation Room 2 | 2.5844 | 10.1716 | 18 | 22.5 | 30.45 | 13.0875 | 344.0348
Private Room 5 | 2.5844 | 15.8619 | 18 | 22.5 | 30.45 | 13.0875 | 536.4982
Private Room 6 | 2.5844 | 15.8619 | 18 | 22.5 | 30.45 | 13.0875 | 536.4982
3-Bed Ward 1 | 2.5844 | 24.783 | 18 | 22.5 | 30.45 | 13.0875 | 838.2372
3-Bed Ward 2 | 2.5844 | 24.8909 | 18 | 22.5 | 30.45 | 13.0875 | 841.8867
Private Room 7 | 2.5844 | 13.6813 | 18 | 22.5 | 30.45 | 13.0875 | 462.7436
Private Room 8 | 2.5844 | 13.7512 | 18 | 22.5 | 30.45 | 13.0875 | 465.1078
Private Room 9 | 2.5844 | 16.0112 | 18 | 22.5 | 30.45 | 13.0875 | 541.548
Private Room 10 | 2.5844 | 16.0112 | 18 | 22.5 | 30.45 | 13.0875 | 541.548
Elevator | 2.5844 | 8.9651 | 18 | 22.5 | 30.45 | 13.0875 | 303.2272
Private Room 11 | 2.5844 | 13.7512 | 18 | 22.5 | 30.45 | 13.0875 | 465.1078
Private Room 12 | 2.5844 | 13.7512 | 18 | 22.5 | 30.45 | 13.0875 | 465.1078
Waiting Area | 2.5844 | 23.4829 | 18 | 22.5 | 30.45 | 13.0875 | 794.2638
Private Room 13 | 2.5844 | 10.7572 | 18 | 22.5 | 30.45 | 13.0875 | 363.8416
Private Room 14 | 2.5844 | 11.315 | 18 | 22.5 | 30.45 | 13.0875 | 382.7081
Solarium 1 | 2.5844 | 13.3083 | 18 | 22.5 | 30.45 | 13.0875 | 450.1276
Stretcher's Wheelchair Nook 1 | 2.5844 | 11.0872 | 18 | 22.5 | 30.45 | 13.0875 | 375.0032
Stretcher's Wheelchair Nook 2 | 2.5844 | 8.275 | 18 | 22.5 | 30.45 | 13.0875 | 279.8859
Solarium 2 | 2.5844 | 13.4675 | 18 | 22.5 | 30.45 | 13.0875 | 455.5122
Water Tank 1 and 2 | 2.5844 | 183.9438 | 18 | 22.5 | 30.45 | 13.0875 | 6221.5446
Chapel | 2.5844 | 58.8601 | 18 | 22.5 | 30.45 | 13.0875 | 1990.8295
Waiting Area | 2.5844 | 43.5914 | 18 | 22.5 | 30.45 | 13.0875 | 1474.3951
Admitting | 2.5844 | 10.9006 | 18 | 22.5 | 30.45 | 13.0875 | 368.6918
Billing | 2.5844 | 10.7831 | 18 | 22.5 | 30.45 | 13.0875 | 364.7176
Cashier | 2.5844 | 9.4163 | 18 | 22.5 | 30.45 | 13.0875 | 318.4882
Personel's dining | 2.5844 | 26.9958 | 18 | 22.5 | 30.45 | 13.0875 | 913.0809
[6 empty] | Total Load | 33124.8407

## PARTITION LOAD
Space | Spaces | U | A | Ti | Ti2 | Q
Power House | Hallway | 2.7144 | 22.2 | 22.5 | 28 | 331.4282 |  | 1.8 | 24
| Work Area | 2.7144 | 14.52 | 22.5 | 22.5 | 0 |  | 0 | 14.52
| Storage Room | 2.7144 | 11.6 | 22.5 | 24 | 47.2306 |  | 0 | 11.6
Work Area | Storage Room | 2.7144 | 10.2 | 22.5 | 24 | 41.5303 |  | 1.8 | 12
| Maintenance Room | 2.7144 | 12.72 | 22.5 | 22.5 | 0 |  | 1.8 | 14.52
Storage Room | Hallway | 2.7144 | 12 | 24 | 28 | 130.2912 |  | 0 | 12
| Maintenance Room | 2.7144 | 11.6 | 24 | 22.5 | 47.2306 |  | 0 | 11.6
Maintenance Room | Hallway | 2.7144 | 28 | 22.5 | 28 | 418.0176 |  | 1.8 | 29.8
| Maintenance Room CR | 2.7144 | 11.68 | 22.5 | 24 | 47.5563 |  | 1.8 | 13.48
Female Toilet | Hallway | 2.7144 | 36.2 | 24 | 28 | 393.0451 |  | 1.8 | 38
Male Toilet | Hallway | 2.7144 | 36.2 | 24 | 28 | 393.0451 |  | 1.8 | 38
Minor Operating Room | Hallway | 2.7144 | 24.2 | 22 | 28 | 394.1309 |  | 1.8 | 26
| Emergency Room | 2.7144 | 18.8 | 22 |  | 1122.6758 |  | 3.6 | 22.4
| Examination/Treatment OBS CR | 2.7144 | 7.72 | 22 | 24 | 41.9103 |  | 0 | 7.72
| Equipment and Supply Storage Area | 2.7144 | 11.2 | 22 | 24 | 60.8026 |  | 0 | 11.2
Equipment and Supply Storage | Emergency Room | 2.7144 | 7 | 24 |  | 456.0192 |  | 1.8 | 8.8
| Examination/Treatment OBS CR | 2.7144 | 8.8 | 24 | 24 | 0 |  | 0 | 8.8
Examination/Treatment OBS | Examination/Treatment OBS CR | 2.7144 | 5.92 | 22.5 | 24 | 24.1039 |  | 1.8 | 7.72
Emergency Room | Hallway | 2.7144 | 36.2 |  | 28 | 2751.3158 |  |  | 36.2
| Doctor's on Duty CR | 2.7144 | 3.4 |  | 24 | 221.495 |  | 1.8 | 5.2
| Doctor's on Duty | 2.7144 | 23.76 |  | 22.5 | 1451.1182 |  | 1.8 | 25.56
Doctor's on Duty | Doctor's on Duty CR | 2.7144 | 10.4 | 22.5 | 24 | 42.3446 | 0 | 0 | 10.4
| Hallway | 2.7144 | 10.6 | 22.5 | 28 | 158.2495 | 1.4 | 0 | 12
Cadaver Holding Room | Hallway | 2.7144 | 10.4 | 22.5 | 28 | 155.2637 | 0 | 3.6 | 14
| Supply Room | 2.7144 | 0 | 22.5 | 24 | 0
| Work Area Laboratory | 2.7144 | 5.2 | 22.5 |  | 317.5848 | 0 | 0 | 5.2
Supply Room | Hallway | 2.7144 | 0 | 24 | 28 | 0
| Pathology Office Laboratory | 2.7144 | 22 | 24 |  | 1433.2032 | 0 | 0 | 22
Pharmacy | Bulk Storage | 2.7144 | 15.4 | 22.5 | 24 | 62.7026 |  | 1.8 | 17.2
| Hallway | 2.7144 | 54.2 | 22.5 | 28 | 809.1626 | 2.8 | 1.8 | 58.8
| Medical Record Office | 2.7144 | 24 | 22.5 | 22.5 | 0 | 0 | 0 | 24
Bulk Storage | Hallway | 2.7144 | 16.8 | 24 | 28 | 182.4077 | 0 | 0 | 16.8
Medical Record Office | Hallway | 2.7144 | 45.32 | 22.5 | 28 | 676.5913 | 4.08 | 1.8 | 51.2
| Philhealth | 2.7144 | 24 | 22.5 | 22.5 | 0 | 0 | 0 | 24
Philhealth | Hallway | 2.7144 | 43.8 | 22.5 | 28 | 653.899 | 2.4 | 1.8 | 48
Work Area Laboratory | Waiting Area CR | 2.7144 | 9 |  | 24 | 586.3104 | 0 | 0 | 9
| Waiting Area | 2.7144 | 19.8 |  | 22.5 | 1209.2652 | 0 | 1.8 | 21.6
| Hallway | 2.7144 | 12.2 |  | 28 | 927.239 | 0 | 0 | 12.2
Film File Storage | Wating Area CR | 2.7144 | 8.8 | 24 | 24 | 0 | 0 | 0 | 8.8
| Waiting Area | 2.7144 | 5.8 | 24 |  | 377.8445 | 0 | 0 | 5.8
| Dark Room | 2.7144 | 14.6 | 24 | 22.5 | 59.4454 | 0 | 0 | 14.6
| Radiologist Office | 2.7144 | 4.84 | 24 | 22.5 | 19.7065 | 0 | 1.8 | 6.64
Waiting Area | Waiting Area CR | 2.7144 | 4.6 | 22.5 | 24 | 18.7294 | 0 | 1.8 | 6.4
| Hallway | 2.7144 | 16 | 22.5 | 28 | 238.8672 | 0 | 2.4 | 18.4
Dark Room | Radiologist Office | 2.7144 | 6 | 22.5 | 22.5 | 0 | 0 | 0 | 6
| Waste Disposal Area | 2.7144 | 6 | 22.5 | 24 | 24.4296 | 0 | 0 | 6
| X-Ray Room CR | 2.7144 | 6.8 | 22.5 | 24 | 27.6869 | 0 | 0 | 6.8
| X Ray Room | 2.7144 | 13 | 22.5 |  | 793.962 | 0 | 1.6 | 14.6
Radiogist Office | Hallway | 2.7144 | 9.4 | 22.5 | 28 | 140.3345 | 1.4 | 1.8 | 12.6
| X Ray Room | 2.7144 | 10.6 | 22.5 |  | 647.3844 | 0 | 1.8 | 12.4
X Ray Room | Waste Disposal Area | 2.7144 | 14.32 |  | 24 | 932.885 | 0 | 0 | 14.32
| Linen Storage | 2.7144 | 19.4 |  | 24 | 1263.8246 | 0 | 0 | 19.4
| Pressing Area | 2.7144 | 3.4 |  | 22.5 | 207.6516 | 0 | 0 | 3.4
| Hallway | 2.7144 | 21.72 |  | 28 | 1650.7895 | 0 | 2.4 | 24.12
Pressing Area | Washing Area | 2.7144 | 10.2 | 22.5 | 24 | 41.5303 | 0 | 1.8 | 12
| Linen Storage | 2.7144 | 10.2 | 22.5 | 24 | 41.5303 | 0 | 1.8 | 12
| Waste Disposal Area | 2.7144 | 8.88 | 22.5 | 24 | 36.1558 | 0 | 0 | 8.88
Linen Storage | Washing Area | 2.7144 | 22 | 24 | 24 | 0 | 0 | 1.8 | 23.8
| Hallway | 2.7144 | 10.72 | 24 | 28 | 116.3935 | 1.4 | 0 | 12.12
Washing Area | Washing Area CR | 2.7144 | 17.2 | 24 | 24 | 0 | 0 | 1.6 | 18.8
| Hallway | 2.7144 | 38 | 24 | 28 | 412.5888 | 0 | 2 | 40
OPD Clinic Dental | Hallway | 2.7144 | 28.4 | 22.5 | 28 | 423.9893 | 1.2 | 2.4 | 32
| OPD Clinic Dental | 2.7144 | 19.44 | 22.5 | 22.5 | 0 | 0 | 0 | 19.44
| OPD Clinic Pedia | 2.7144 | 12.56 | 22.5 | 22.5 | 0 | 0 | 0 | 12.56
OPD Clinic Dental | Hallway | 2.7144 | 18.4 | 22.5 | 28 | 274.6973 | 1.2 | 2.4 | 22
| OPD Clinic Pedia | 2.7144 | 12.56 | 22.5 | 22.5 | 0 | 0 | 0 | 12.56
| Elevator | 2.7144 | 10 | 22.5 |  | 610.74 | 0 | 0 | 10
OPD Clinic Pedia | Hallway | 2.7144 | 28.4 | 22.5 | 28 | 423.9893 | 1.2 | 2.4 | 32
| OPD Clinic Pedia | 2.7144 | 19.44 | 22.5 | 22.5 | 0 | 0 | 0 | 19.44
OPD Clinic Pedia | Hallway | 2.7144 | 8.96 | 22.5 | 28 | 133.7656 | 1.2 | 2.4 | 12.56
| OPD Records | 2.7144 | 9.92 | 22.5 | 22.5 | 0 | 0 | 0 | 9.92
| OPD Info & Admitting | 2.7144 | 9.52 | 22.5 | 22.5 | 0 | 0 | 0 | 9.52
OPD Records | Elevator | 2.7144 | 19.2 | 22.5 |  | 1172.6208 | 0 | 0 | 19.2
| OPD Info & Admitting | 2.7144 | 17.6 | 22.5 | 22.5 | 0 | 0 | 1.6 | 19.2
Elevator | Hallway | 2.7144 | 19.2 |  | 28 | 1459.2614 | 0 | 0 | 19.2
| OPD Clinic Surgery | 2.7144 | 10 |  | 22.5 | 610.74 | 0 | 0 | 10
OPD Info & Admitting | Hallway | 2.7144 | 16.4 | 22.5 | 28 | 244.8389 | 1.2 | 1.6 | 19.2
| OPD Clinic Medical | 2.7144 | 9.52 | 22.5 | 22.5 | 0 | 0 | 0 | 9.52
OPD Clinic Surgery | Hallway | 2.7144 | 18.64 | 22.5 | 28 | 278.2803 | 1.2 | 1.6 | 21.44
| OPD Clinic Surgery | 2.7144 | 19.2 | 22.5 | 22.5 | 0 | 0 | 0 | 19.2
| OPD Clinic Medical | 2.7144 | 12 | 22.5 | 22.5 | 0 | 0 | 0 | 12
OPD Clinic Medical | OPD Clinic Medical | 2.7144 | 19.2 | 22.5 | 22.5 | 0 | 0 | 0 | 19.2
| Hallway | 2.7144 | 9.2 | 22.5 | 28 | 137.3486 | 1.2 | 1.6 | 12
OPD Clinic Surgery | Hallway | 2.7144 | 28.64 | 22.5 | 28 | 427.5723 | 1.2 | 1.6 | 31.44
| OPD Clinic Medical | 2.7144 | 12 | 22.5 | 22.5 | 0 | 0 | 0 | 12
OPD Clinic Medical | Hallway | 2.7144 | 28.64 | 22.5 | 28 | 427.5723 | 1.2 | 1.6 | 31.44
Cashier | Billing | 2.7144 | 12 | 22.5 | 22.5 | 0 | 0 | 0 | 12
| Hallway | 2.7144 | 25.8 | 22.5 | 28 | 385.1734 |  | 1.8 | 27.6
Billing | Hallway | 2.7144 | 13.8 | 22.5 | 28 | 206.023 |  | 1.8 | 15.6
| Admitting | 2.7144 | 12 | 22.5 | 22.5 | 0 |  | 0 | 12
Admitting | Hallway | 2.7144 | 13.8 | 22.5 | 28 | 206.023 |  | 1.8 | 15.6
Administrative Office | Admin Office | 2.7144 | 10.4 | 22.5 | 22.5 | 0 | 0 | 1.8 | 12.2
| Social Welfare | 2.7144 | 12.2 | 22.5 | 22.5 | 0 | 0 | 0 | 12.2
| Hallway | 2.7144 | 63 | 22.5 | 28 | 940.5396 | 7.2 | 1.8 | 72
Admin Office | Social Welfare | 2.7144 | 19.2 | 22.5 | 22.5 | 0 | 0 | 0 | 19.2
| Hallway | 2.7144 | 16.8 | 22.5 | 28 | 250.8106 | 2.4 | 0 | 19.2
| Male Toilet | 2.7144 | 12 | 22.5 | 24 | 48.8592 | 0 | 0 | 12
Social Welfare | Hallway | 2.7144 | 15 | 22.5 | 28 | 223.938 | 2.4 | 1.8 | 19.2
| Female Toilet | 2.7144 | 12 | 22.5 | 24 | 48.8592 | 0 | 0 | 12
Male Toilet | Hallway | 2.7144 | 33 | 24 | 28 | 358.3008 | 1.2 | 1.8 | 36
| Female Toilet | 2.7144 | 24 | 24 | 24 | 0 | 0 | 0 | 24
Female Toilet | Hallway | 2.7144 | 33 | 24 | 28 | 358.3008 | 1.2 | 1.8 | 36
OPD Info & Admitting | Hallway | 2.7144 | 23.84 | 22.5 | 28 | 355.9121 | 1.4 | 1.8 | 27.04
| OPD Records | 2.7144 | 13.84 | 22.5 | 22.5 | 0 | 0 | 1.8 | 15.64
OPD Records | Hallway | 2.7144 | 25.2 | 22.5 | 28 | 376.2158 | 0 | 0 | 25.2
| Ultrasound | 2.7144 | 15.64 | 22.5 | 22.5 | 0 | 0 | 0 | 15.64
Ultrasound | Ultrasound CR | 2.7144 | 11.8 | 22.5 | 24 | 48.0449 | 0 | 1.8 | 13.6
| Hallway | 2.7144 | 25.6 | 22.5 | 28 | 382.1875 | 0 | 1.8 | 27.4
OPD Clinic OB-Gyne | Hallway | 2.7144 | 44 | 22.5 | 28 | 656.8848 | 0 | 2.4 | 46.4
| OPD Clinic OB-Gyne CR | 2.7144 | 11.8 | 22.5 | 24 | 48.0449 | 0 | 1.8 | 13.6
Canteen | Hallway | 2.7144 | 24.12 | 24 | 28 | 261.8853 | 0 | 4 | 28.12
| Dietary | 2.7144 | 28.6 | 24 | 22.5 | 116.4478 | 2.8 | 2.4 | 33.8
Dietary | Hallway | 2.7144 | 98.44 | 22.5 | 28 | 1469.6304 | 0 | 6.6 | 105.04
| Supply Receiving Area | 2.7144 | 21.72 | 22.5 | 22.5 | 0 | 0 | 1.8 | 23.52
| Dietitian Office | 2.7144 | 20.8 | 22.5 | 22.5 | 0 | 2.8 | 1.8 | 25.4
| Dietitians Office CR | 2.7144 | 12.12 | 22.5 | 24 | 49.3478 | 0 | 0 | 12.12
| Cold Storage | 2.7144 | 6.12 | 22.5 | 24 | 24.9182 | 0 | 1.2 | 7.32
| Dry Storage | 2.7144 | 16.76 | 22.5 | 24 | 68.24 | 0 | 1.2 | 17.96
| Garbage Disposal | 2.7144 | 8 | 22.5 | 24 | 32.5728 | 0 | 0 | 8
Supply Receiving Area | Hallway | 2.7144 | 12.92 | 22.5 | 28 | 192.8853 | 0 | 0 | 12.92
| Cold Storage | 2.7144 | 5.04 | 22.5 | 24 | 20.5209 | 0 | 0 | 5.04
Cold Storage | Dry Storage | 2.7144 | 5.08 | 24 | 24 | 0 | 0 | 0 | 5.08
| Hallway | 2.7144 | 6.8 | 24 | 28 | 73.8317 | 0 | 0 | 6.8
Dry Storage | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Dietitians Office | Dietitians Office CR | 2.7144 | 4.92 | 22.5 | 24 | 20.0323 | 0 | 1.6 | 6.52
[5 empty] | Total | 36547.3873
Second Floor
Space | Spaces | U | A | Ti | Ti2 | Q | Window | Door | Wall
5 Bedward | Hallway | 2.7144 | 16.4 | 22.5 | 28 | 244.8389 | 0 | 2.4 | 18.8
| 5 Bedward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
5 Bedward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
5 Bedward | Hallway | 2.7144 | 42.4 | 22.5 | 28 | 632.9981 | 0 | 2.4 | 44.8
| 5 Bedward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
5 Bedward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
5 Bedward | Hallway | 2.7144 | 42.2 | 22.5 | 28 | 630.0122 | 0 | 2.4 | 44.6
| 5 Bedward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
5 Bedward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
5 Bedward | Hallway | 2.7144 | 16.4 | 22.5 | 28 | 244.8389 | 0 | 2.4 | 18.8
| 5 Bedward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
5 Bedward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Isolation Room | Hallway | 2.7144 | 0 | 22.2 | 28 | 0
| Isolation Room CR | 2.7144 | 0 | 22.5 | 24 | 0
Isolation Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885 | 0 | 2.4 | 6.8
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
| Chief of Hospital CR | 2.7144 | 3 | 22.5 | 24 | 12.2148 | 0 | 0 | 3
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 28.4 | 22.5 | 28 | 423.9893 | 0 | 2.4 | 30.8
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Chief Nurse | Hallway | 2.7144 | 63.6 | 22.5 | 28 | 949.4971 | 0 | 1.8 | 65.4
| Chief Nurse CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Chief Nurse CR | Hallway | 2.7144 | 14.8 | 24 | 28 | 160.6925 | 0 | 0 | 14.8
Treatment Room | Hallway | 2.7144 | 51.8 | 22.5 | 28 | 773.3326 | 0 | 2.4 | 54.2
Dirty Utility | Hallway | 2.7144 | 29.76 | 24 | 28 | 323.1222 | 0 | 1.2 | 30.96
Clean Linen | Hallway | 2.7144 | 11.44 | 24 | 28 | 124.2109 | 0 | 1.2 | 12.64
Nurse Station CR | Hallway | 2.7144 | 18.72 | 24 | 28 | 203.2543 | 0 | 1.2 | 19.92
Private Room | Hallway | 2.7144 | 28.2 | 22.5 | 28 | 421.0034 | 0 | 2.4 | 30.6
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885 | 0 | 2.4 | 6.8
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Isolation Room | Hallway | 2.7144 | 0 | 22.5 | 28 | 0
| Isolation Room CR | 2.7144 | 0 | 22.5 | 24 | 0
Isolation Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 |  |  | 5.4
Reception | Chief of Hospital CR | 2.7144 | 12 | 22.5 | 24 | 48.8592 | 0 | 0 | 12
| Hallway | 2.7144 | 10.4 | 22.5 | 28 | 155.2637 | 0 | 1.6 | 12
Chief of Hospital | Hallway | 2.7144 | 10.2 | 22.5 | 28 | 152.2778 | 0 | 1.8 | 12
| Chief of Hospital CR | 2.7144 | 9.6 | 22.5 | 24 | 39.0874 | 0 | 1.2 | 10.8
Conference Room | Hallway | 2.7144 | 22 | 22.5 | 28 | 328.4424 | 0 | 2 | 24
Chief of Clinics | Hallway | 2.7144 | 13.2 | 22.5 | 28 | 197.0654 | 0 | 1.8 | 15
| Labor Room CR | 2.7144 | 12 | 22.5 | 24 | 48.8592 | 0 | 0 | 12
| Chief of Clinics CR | 2.7144 | 10.4 | 22.5 | 24 | 42.3446 | 0 | 1.2 | 11.6
| Delivery Room | 2.7144 | 15.32 | 22.5 | 22 | 20.7923 | 0 | 0 | 15.32
3 Bed Ward | 3 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
| Hallway | 2.7144 | 51.52 | 22.5 | 28 | 769.1524 | 0 | 2.4 | 53.92
3 Bed Ward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
3 Bed Ward | 3 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
| Hallway | 2.7144 | 54.68 | 22.5 | 28 | 816.3287 | 0 | 2.4 | 57.08
3 Bed Ward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Elevator | Hallway | 2.7144 | 36.16 | 22.5 | 28 | 539.8399 | 0 |  | 36.16
3 Bed Ward | 3 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
| Hallway | 2.7144 | 47 | 22.5 | 28 | 701.6724 | 0 | 1.6 | 48.6
3 Bed Ward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
3 Bed Ward | 3 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
| Hallway | 2.7144 | 56.08 | 22.5 | 28 | 837.2295 | 0 | 2.4 | 58.48
3 Bed Ward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885 | 0 | 2.4 | 6.8
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885 | 0 | 2.4 | 6.8
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885 | 0 | 2.4 | 6.8
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885 | 0 | 2.4 | 6.8
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Delivery Room | Labor Room CR | 2.7144 | 6.2 | 22 | 24 | 33.6586 | 0 | 0 | 6.2
| Subster Room | 2.7144 | 6.6 | 22 | 22.5 | 8.9575 | 0 | 1.8 | 8.4
| Hallway | 2.7144 | 30.6 | 22 | 28 | 498.3638 | 0 | 3.2 | 33.8
Subster Room | Labor Room CR | 2.7144 | 12 | 22.5 | 24 | 48.8592 | 0 | 0 | 12
| Hallway | 2.7144 | 11.2 | 22.5 | 28 | 167.207 | 0.8 | 0 | 12
Labor Room | Hallway | 2.7144 | 39 | 22.5 | 28 | 582.2388 | 1.6 | 5.2 | 45.8
Pathologic Nursery | Hallway | 2.7144 | 15.6 | 22.5 | 28 | 232.8955 | 2.4 | 0 | 18
Pre-mature Nursery | Hallway | 2.7144 | 15.92 | 22.5 | 28 | 237.6729 | 2.4 | 0 | 18.32
Breastfeeding Room | Hallway | 2.7144 | 9 | 22.5 | 28 | 134.3628 | 0.8 | 1.6 | 11.4
| Pre-Operation Area | 2.7144 | 15.6 | 22.5 | 22 | 21.1723 | 0 | 0 | 15.6
Work Area | Hallway | 2.7144 | 48 | 22.5 | 28 | 716.6016 | 0 | 0 | 48
| Pre-Operation Area | 2.7144 | 5.4 | 22.5 | 22 | 7.3289 | 1.4 | 1.8 | 8.6
Pre Operation Area | Hallway | 2.7144 | 48.8 | 22 | 28 | 794.7763 | 1.4 | 1.8 | 52
CSSR | Hallway | 2.7144 | 52.72 | 22.5 | 28 | 787.0674 | 3.8 | 2 | 58.52
| Autoclave Area CR | 2.7144 | 17 | 22.5 | 24 | 69.2172 | 0 | 0.6 | 17.6
| Sterile Supply Room | 2.7144 | 24.12 | 22.5 | 24 | 98.207 | 0 | 1.8 | 25.92
Sterile Supply Room | Recovery Room | 2.7144 | 12 | 24 | 22.5 | 48.8592 | 0 | 0 | 12
Recovery Room | Hallway | 2.7144 | 24.6 | 22.5 | 28 | 367.2583 | 0 | 3.2 | 27.8
| Recovery Room CR | 2.7144 | 11.96 | 22.5 | 24 | 48.6963 | 0 | 1.2 | 13.16
Major Operating Room | Hallway | 2.7144 | 36.2 | 22 | 28 | 589.5677 | 0 | 3.2 | 39.4
| Subster Room | 2.7144 | 7.2 | 22 | 22.5 | 9.7718 | 0 | 1.8 | 9
Subster Room | Clean up Room | 2.7144 | 9 | 22.5 | 24 | 36.6444 | 0 | 0 | 9
| Hallway | 2.7144 | 10.72 | 22.5 | 28 | 160.041 | 0.8 | 0 | 11.52
Clean up Room | Hallway | 2.7144 | 7 | 24 | 28 | 76.0032 | 0 | 2 | 9
Jan. Clo | Hallway | 2.7144 | 16.8 | 24 | 28 | 182.4077 | 0 | 1.4 | 18.2
Sterile Instrument Supply | Hallway | 2.7144 | 9.92 | 24 | 28 | 107.7074 | 0 | 1.6 | 11.52
Anesthesia Office & Storage | Hallway | 2.7144 | 22.52 | 24 | 28 | 244.5132 | 0.8 | 1.8 | 25.12
DR 1 | Lounge Area | 2.7144 | 5 | 24 | 22.5 | 20.358 | 0 | 1.2 | 6.2
DR 2 | Lounge Area | 2.7144 | 5 | 24 | 22.5 | 20.358 | 0 | 1.2 | 6.2
DR 3 | Lounge Area | 2.7144 | 23 | 24 | 22.5 | 93.6468 | 0 | 1.2 | 24.2
Lounge Area | Hallway | 2.7144 | 60.6 | 22 | 28 | 986.9558 | 0 | 3.4 | 64
[5 empty] | Total | 19649.5959
Space | Spaces | U | A | Ti | Ti2 | Q | Window | Door | Wall
5 Bed Ward | Hallway | 2.7144 | 16.4 | 22.5 | 28 | 244.8389 | 0 | 2.4 | 18.8
| 5 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
5 Bed Ward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
5 Bed Ward | Hallway | 2.7144 | 42.4 | 22.5 | 28 | 632.9981 | 0 | 2.4 | 44.8
| 5 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
5 Bed Ward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
5 Bed Ward | Hallway | 2.7144 | 42.4 | 22.5 | 28 | 632.9981 | 0 | 2.4 | 44.8
| 5 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
5 Bed Ward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
5 Bed Ward | Hallway | 2.7144 | 16.4 | 22.5 | 28 | 244.8389 | 0 | 2.4 | 18.8
| 5 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
5 Bed Ward CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Isolation Room | Hallway | 2.7144 | 0 | 22.5 | 28 | 0
| Isolation Room CR | 2.7144 | 0 | 22.5 | 24 | 0
Isolation Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885 | 0 | 2.4 | 6.8
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 30.8 | 22.5 | 28 | 459.8194 | 0 | 0 | 30.8
| Private Room CR | 2.7144 | 14.8 | 22.5 | 24 | 60.2597 | 0 | 0 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Chief Nurse | Hallway | 2.7144 | 62.4 | 22.5 | 28 | 931.5821 | 1.2 | 1.8 | 65.4
| Chief Nurse CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Chief Nurse CR | Hallway | 2.7144 | 14.8 | 24 | 28 | 160.6925 | 0 | 0 | 14.8
Treatment Room | Hallway | 2.7144 | 60.2 | 22.5 | 28 | 898.7378 | 1.2 | 2.4 | 63.8
Dirty Utility | Hallway | 2.7144 | 29.76 | 24 | 28 | 323.1222 | 0 | 1.2 | 30.96
Clean Utility | Hallway | 2.7144 | 11.44 | 24 | 28 | 124.2109 | 0 | 1.2 | 12.64
Nurse Station CR | Hallway | 2.7144 | 18.72 | 24 | 28 | 203.2543 | 0 | 1.2 | 19.92
Private Room | Hallway | 2.7144 | 28.4 | 22.5 | 28 | 423.9893 | 0 | 2.4 | 30.8
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885 | 0 | 2.4 | 6.8
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Isolation Room | Hallway | 2.7144 | 0 | 22.5 | 28 | 0
| Isolation Room CR | 2.7144 | 0 | 22.5 | 24 | 0
Isolation Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885 | 0 | 2.4 | 6.8
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885 | 0 | 2.4 | 6.8
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885 | 0 | 2.4 | 6.8
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885 | 0 | 2.4 | 6.8
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Solarium | Hallway | 2.7144 | 11.8 | 22.5 | 28 | 176.1646 | 0.8 | 2.4 | 15
| Water Tank | 2.7144 | 15.2 | 22.5 | 24 | 61.8883 | 0 | 0 | 15.2
3 Bed Ward | Hallway | 2.7144 | 42.08 | 22.5 | 28 | 628.2207 | 0 | 2.4 | 44.48
| 3 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
| Elevator | 2.7144 | 0 | 22.5 |  | 0
3 Bed Ward CR | Hallway | 2.7144 | 9.4 | 24 | 28 | 102.0614 | 0 | 0 | 9.4
| Private Room | 2.7144 | 5.4 | 24 | 22.5 | 21.9866 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 24.76 | 22.5 | 28 | 369.647 | 0 | 2.4 | 27.16
| Private Room CR | 2.7144 | 13.44 | 22.5 | 24 | 54.7223 | 0 | 1.4 | 14.84
Private Room CR | Hallway | 2.7144 | 5.44 | 24 | 28 | 59.0653 | 0 | 0 | 5.44
Private Room | Hallway | 2.7144 | 24.36 | 22.5 | 28 | 363.6753 | 0 | 2.4 | 26.76
| Private Room CR | 2.7144 | 13.36 | 22.5 | 24 | 54.3966 | 0 | 1.4 | 14.76
Private Room CR | Hallway | 2.7144 | 5.36 | 24 | 28 | 58.1967 | 0 | 0 | 5.36
Elevator | Hallway | 2.7144 | 0 |  | 28 | 0
| 3 Bed Ward | 2.7144 | 9.4 |  | 22.5 | 574.0956 | 0 | 0 | 9.4
3 Bed Ward | Hallway | 2.7144 | 42.2 | 22.5 | 28 | 630.0122 | 0 | 2.4 | 44.6
| 3 Bed Ward CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
3 Bed Ward CR | Hallway | 2.7144 | 9.4 | 24 | 28 | 102.0614 | 0 | 0 | 9.4
| Private Room | 2.7144 | 5.4 | 24 | 22.5 | 21.9866 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 24.36 | 22.5 | 28 | 363.6753 | 0 | 2.4 | 26.76
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 24.84 | 22.5 | 28 | 370.8413 | 0 | 2.4 | 27.24
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885 | 0 | 2.4 | 6.8
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885 | 0 | 2.4 | 6.8
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885 | 0 | 2.4 | 6.8
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Private Room | Hallway | 2.7144 | 4.4 | 22.5 | 28 | 65.6885 | 0 | 2.4 | 6.8
| Private Room CR | 2.7144 | 13.4 | 22.5 | 24 | 54.5594 | 0 | 1.4 | 14.8
Private Room CR | Hallway | 2.7144 | 5.4 | 24 | 28 | 58.631 | 0 | 0 | 5.4
Solarium | Hallway | 2.7144 | 11.8 | 22.5 | 28 | 176.1646 | 0.8 | 2.4 | 15
Waiting Area | Hallway | 2.7144 | 52.8 | 22.5 | 28 | 788.2618 | 0 | 3.2 | 56
| Personel's Dining | 2.7144 | 8.8 | 22.5 | 24 | 35.8301 | 0 | 3.2 | 12
Cashier | Personel's Dining | 2.7144 | 12 | 22.5 | 24 | 48.8592 | 0 | 0 | 12
Personel's Dining | Hallway | 2.7144 | 22.4 | 24 | 28 | 243.2102 | 0 | 0 | 22.4
Female Toilet | Hallway | 2.7144 | 34.92 | 24 | 28 | 379.1474 | 0 | 1.8 | 36.72
Male Toilet | Hallway | 2.7144 | 10.72 | 24 | 28 | 116.3935 | 0 | 1.8 | 12.52
Water Tank | Hallway | 2.7144 | 21.4 | 24 | 28 | 232.3526 |  |  | 21.4
14294.9533

## VENTILATION LOAD
VENTILATION LOAD
FIRST FLOOR
SPACE | Occ | L/s | To | Ti | Wo | Wi | Qs (W) | Qw (W) | L/s-person
Maintenance Office | 3 | 24 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 354.816 | 695.2422 | 8
Minor Operating Room | 6 | 90 | 34.5 | 22 | 0.018137 | 0.0082198 | 1386 | 2677.5878 | 15
Examination/Treatment Area | 6 | 48 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 709.632 | 1390.4844 | 8
Supply Room | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 2.5
Pharmacy | 4 | 32 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 473.088 | 926.9896 | 8
Medical Records Office | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 2.5
PHILHEALTH | 5 | 40 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 591.36 | 1158.737 | 8
Doctor's Duty | 4 | 10 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 147.84 | 289.6843 | 2.5
Nurse Station | 6 | 48 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 709.632 | 1390.4844 | 8
Work Area Laboratory | 4 | 40 | 34.5 | 22 | 0.018137 | 0.0082198 | 616 | 1190.039 | 10
OPD Clinic Dental | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 2.5
OPD Clinic Dental | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 2.5
OPD Clinic Surgery | 3 | 7.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 110.88 | 217.2632 | 2.5
OPD Clinic Surgery | 3 | 7.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 110.88 | 217.2632 | 2.5
Cashier | 1 | 2.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.96 | 72.4211 | 2.5
Billing | 1 | 2.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.96 | 72.4211 | 2.5
Admitting | 1 | 2.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.96 | 72.4211 | 2.5
Radiologist Office | 5 | 12.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 184.8 | 362.1053 | 2.5
Dark Room | 3 | 24 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 354.816 | 695.2422 | 8
Control Booth | 4 | 32 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 473.088 | 926.9896 | 8
OPD Clinic Pedia | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 2.5
OPD Clinic Pedia | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 2.5
OPD info. And Admitting | 3 | 0 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 0 | 0
OPD Clinic Medical | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 2.5
OPD Clinic Medical | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 2.5
Admin Office | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 2.5
Administrative Office | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 2.5
Social Welfare | 3 | 7.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 110.88 | 217.2632 | 2.5
OPD Info. And Admitting | 3 | 7.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 110.88 | 217.2632 | 2.5
OPD Records |  | 0 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 0 | 0
Ultrasound | 4 | 32 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 473.088 | 926.9896 | 8
Supply Receiving Area | 2 | 5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 73.92 | 144.8421 | 2.5
Dietician's Office | 3 | 7.5 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 110.88 | 217.2632 | 2.5
Dietary | 3 | 0 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 0 | 0
Staff Dining | 8 | 64 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 946.176 | 1853.9793 | 8
OPD clinic Ob-gyne | 4 | 10 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 147.84 | 289.6843 | 2.5
Canteen | 20 | 160 | 34.5 | 24 | 0.018137 | 0.0092932 | 2069.76 | 4244.8882 | 8
[7 empty] | 11116.336 | 21915.97
SECOND FLOOR
SPACE | Occ. | L/s | To | Ti | Wo | Wi | Qs(W) | Ql(W) | L/s-person
5-Bed Ward 1 | 5 | 65 | 34.5 | 22.5 | 0.018137 | #NAME? | 960.96 | #NAME? | 13
5-Bed Ward 2 | 5 | 65 | 34.5 | 22.5 | 0.018137 | #NAME? | 960.96 | #NAME? | 13
5-Bed Ward 3 | 5 | 65 | 34.5 | 22.5 | 0.018137 | #NAME? | 960.96 | #NAME? | 13
5-Bed Ward 4 | 5 | 65 | 34.5 | 22.5 | 0.018137 | #NAME? | 960.96 | #NAME? | 13
Isolation Room 1 | 3 | 39 | 34.5 | 22.5 | 0.018137 | #NAME? | 576.576 | #NAME? | 13
Private Room 1 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 2 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Chief Nurse | 4 | 10 | 34.5 | 22.5 | 0.018137 | #NAME? | 147.84 | #NAME? | 2.5
Treatment Room | 3 | 24 | 34.5 | 22.5 | 0.018137 | #NAME? | 354.816 | #NAME? | 8
Nurse Station | 8 | 64 | 34.5 | 22.5 | 0.018137 | #NAME? | 946.176 | #NAME? | 8
Dirty Utility | 1 | 2.5 | 34.5 | 24 | 0.018137 | #NAME? | 32.34 | #NAME? | 2.5
Clean Linen | 1 | 2.5 | 34.5 | 24 | 0.018137 | #NAME? | 32.34 | #NAME? | 2.5
Private Room 3 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 4 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Isolation Room 2 | 3 | 39 | 34.5 | 22.5 | 0.018137 | #NAME? | 576.576 | #NAME? | 13
Reception | 5 | 65 | 34.5 | 22.5 | 0.018137 | #NAME? | 960.96 | #NAME? | 13
Private Room 5 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Chief of Hospital | 4 | 0 | 34.5 | 22.5 | 0.018137 | #NAME? | 0 | #NAME?
3-Bed Ward 1 | 3 | 39 | 34.5 | 22.5 | 0.018137 | #NAME? | 576.576 | #NAME? | 13
3-Bed Ward 2 | 3 | 39 | 34.5 | 22.5 | 0.018137 | #NAME? | 576.576 | #NAME? | 13
Private Room 6 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Conference Room | 20 | 260 | 34.5 | 22.5 | 0.018137 | #NAME? | 3843.84 | #NAME? | 13
3-Bed Ward 3 | 3 | 39 | 34.5 | 22.5 | 0.018137 | #NAME? | 576.576 | #NAME? | 13
3-Bed Ward 4 | 3 | 39 | 34.5 | 22.5 | 0.018137 | #NAME? | 576.576 | #NAME? | 13
3-Bed Ward 4 CR |  | 0 | 34.5 | 24 | 0.018137 | #NAME? | 0 | #NAME?
Private Room 7 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 8 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Chief of Clinics | 4 | 10 | 34.5 | 22.5 | 0.018137 | #NAME? | 147.84 | #NAME? | 2.5
Delivery Room | 5 | 40 | 34.5 | 22 | 0.018137 | #NAME? | 616 | #NAME? | 8
Sub-Ster Room 1 | 2 | 5 | 34.5 | 24 | 0.018137 | #NAME? | 64.68 | #NAME? | 2.5
Labor Room | 3 | 24 | 34.5 | 22.5 | 0.018137 | #NAME? | 354.816 | #NAME? | 8
Pathologic Nursery | 4 | 10 | 34.5 | 22.5 | 0.018137 | #NAME? | 147.84 | #NAME? | 2.5
Pre-mature nursery | 10 | 25 | 34.5 | 22.5 | 0.018137 | #NAME? | 369.6 | #NAME? | 2.5
Breastfeeding room | 3 | 7.5 | 34.5 | 22.5 | 0.018137 | #NAME? | 110.88 | #NAME? | 2.5
Pre-operation area | 4 | 60 | 34.5 | 22 | 0.018137 | #NAME? | 924 | #NAME? | 15
Autoclave area | 4 | 32 | 34.5 | 22.5 | 0.018137 | #NAME? | 473.088 | #NAME? | 8
Sterile Supply room | 2 | 5 | 34.5 | 24 | 0.018137 | #NAME? | 64.68 | #NAME? | 2.5
Major Operating Room | 5 | 75 | 34.5 | 22 | 0.018137 | #NAME? | 1155 | #NAME? | 15
Sub-Ster Room 2 | 2 | 5 | 34.5 | 24 | 0.018137 | #NAME? | 64.68 | #NAME? | 2.5
Jan.Clo. | 2 | 5 | 34.5 | 24 | 0.018137 | #NAME? | 64.68 | #NAME? | 2.5
Clean up room | 2 | 5 | 34.5 | 24 | 0.018137 | #NAME? | 64.68 | #NAME? | 2.5
Sterile Instrument Supply Storage Area | 5 | 12.5 | 34.5 | 24 | 0.018137 | #NAME? | 161.7 | #NAME? | 2.5
Anesthesia Office & Storage | 2 | 5 | 34.5 | 24 | 0.018137 | #NAME? | 64.68 | #NAME? | 2.5
Lounge Area | 3 | 24 | 34.5 | 22.5 | 0.018137 | #NAME? | 354.816 | #NAME? | 8
Recovery Room | 3 | 24 | 34.5 | 22.5 | 0.018137 | #NAME? | 354.816 | #NAME? | 8
THIRD FLOOR
Space | Occ. | L/s | To | Ti | Wo | Wi | Qs(W) | Ql(W) | L/s-person
5-Bed Ward 1 | 5 | 65 | 34.5 | 22.5 | 0.018137 | #NAME? | 960.96 | #NAME? | 13
5-Bed Ward 2 | 5 | 65 | 34.5 | 22.5 | 0.018137 | #NAME? | 960.96 | #NAME? | 13
5-Bed Ward 3 | 5 | 65 | 34.5 | 22.5 | 0.018137 | #NAME? | 960.96 | #NAME? | 13
5-Bed Ward 4 | 5 | 65 | 34.5 | 22.5 | 0.018137 | #NAME? | 960.96 | #NAME? | 13
Isolation Room 1 | 3 | 39 | 34.5 | 22.5 | 0.018137 | #NAME? | 576.576 | #NAME? | 13
Private Room 1 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 2 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Chief Nurse | 4 | 10 | 34.5 | 22.5 | 0.018137 | #NAME? | 147.84 | #NAME? | 2.5
Treatment Room | 3 | 24 | 34.5 | 22.5 | 0.018137 | #NAME? | 354.816 | #NAME? | 8
Private Room 3 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 4 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Isolation Room 2 | 3 | 39 | 34.5 | 22.5 | 0.018137 | #NAME? | 576.576 | #NAME? | 13
Private Room 5 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 6 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
3-Bed Ward 1 | 3 | 39 | 34.5 | 22.5 | 0.018137 | #NAME? | 576.576 | #NAME? | 13
3-Bed Ward 2 | 3 | 39 | 34.5 | 22.5 | 0.018137 | #NAME? | 576.576 | #NAME? | 13
Private Room 7 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 8 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 9 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 10 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 11 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 12 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 13 | 2 | 26 | 34.5 | 22.5 | 0.018137 | #NAME? | 384.384 | #NAME? | 13
Private Room 14 | 2 | 0 | 34.5 | 22.5 | 0.018137 | #NAME? | 0 | #NAME?
Solarium 1 | 2 | 5 | 34.5 | 22.5 | 0.018137 | #NAME? | 73.92 | #NAME? | 2.5
Solarium 2 | 2 | 5 | 34.5 | 22.5 | 0.018137 | #NAME? | 73.92 | #NAME? | 2.5
Admitting | 1 | 2.5 | 34.5 | 22.5 | 0.018137 | #NAME? | 36.96 | #NAME? | 2.5
Billing | 1 | 2.5 | 34.5 | 22.5 | 0.018137 | #NAME? | 36.96 | #NAME? | 2.5
Cashier | 1 | 2.5 | 34.5 | 22.5 | 0.018137 | #NAME? | 36.96 | #NAME? | 2.5
Personel's dining | 10 | 80 | 34.5 | 22.5 | 0.018137 | #NAME? | 1182.72 | #NAME? | 8

## OCCUPANT LOAD
OCCUPANT LOAD
FIRST FLOOR
SPACE | Occ | Gain/person | Sensible | Latent | CLF | Qs (W) | Ql (W)
1.4 Maintenance Office | 3 | 70 | 0.6 | 0.4 | 0.92 | 115.92 | 25.76
1.7 Minor Operating Room | 6 | 150 | 0.5 | 0.5 | 0.92 | 414 | 69
1.9 Examination/Treatment Area | 6 | 100 | 0.6 | 0.4 | 0.92 | 331.2 | 36.8
1.11 Supply Room | 2 | 150 | 0.5 | 0.5 | 0.92 | 138 | 69
1.13 Pharmacy | 4 | 150 | 0.5 | 0.5 | 0.92 | 276 | 69
1.14 Medical Records Office | 2 | 150 | 0.55 | 0.45 | 0.92 | 151.8 | 62.1
1.16 PHILHEALTH | 5 | 150 | 0.55 | 0.45 | 0.92 | 379.5 | 62.1
1.17 Doctor's Duty | 4 | 100 | 0.6 | 0.4 | 0.92 | 220.8 | 36.8
1.18 Nurse Station (ER) | 6 | 100 | 0.6 | 0.4 | 0.92 | 331.2 | 36.8
1.21 Work Area (laboratory) | 4 | 150 | 0.5 | 0.5 | 0.92 | 276 | 69
1.24 OPD clinic dental 1 | 2 | 150 | 0.5 | 0.5 | 0.92 | 138 | 69
1.25 OPD clinic dental 2 | 2 | 150 | 0.5 | 0.5 | 0.92 | 138 | 69
1.27 OPD clinic surgery 1 | 3 | 150 | 0.5 | 0.5 | 0.92 | 207 | 69
1.28 OPD clinic surgery 2 | 3 | 150 | 0.5 | 0.5 | 0.92 | 207 | 69
1.29 Cashier | 1 | 150 | 0.55 | 0.45 | 0.92 | 75.9 | 62.1
1.30 Billing | 1 | 150 | 0.55 | 0.45 | 0.92 | 75.9 | 62.1
1.31 Admitting | 1 | 150 | 0.55 | 0.45 | 0.92 | 75.9 | 62.1
1.33 Radiologist Office | 5 | 150 | 0.5 | 0.5 | 0.92 | 345 | 69
1.34 Dark Room | 3 | 100 | 0.6 | 0.4 | 0.92 | 165.6 | 36.8
1.35 Control Booth | 4 | 100 | 0.6 | 0.4 | 0.92 | 220.8 | 36.8
1.37 OPD Clinic Pedia 1 | 2 | 100 | 0.6 | 0.4 | 0.92 | 110.4 | 36.8
1.38 OPD Clinic Pedia 2 | 2 | 100 | 0.6 | 0.4 | 0.92 | 110.4 | 36.8
1.40 OPD info. And admitting | 3 | 150 | 0.55 | 0.45 | 0.92 | 227.7 | 62.1
1.41 OPD Clinic Medical 1 | 2 | 100 | 0.6 | 0.4 | 0.92 | 110.4 | 36.8
1.42 OPD Clinic Medical 2 | 2 | 100 | 0.6 | 0.4 | 0.92 | 110.4 | 36.8
1.50 Admin Office | 2 | 150 | 0.55 | 0.45 | 0.92 | 151.8 | 62.1
1.55 Administrative office | 2 | 150 | 0.55 | 0.45 | 0.92 | 151.8 | 62.1
1.56 Social Welfare | 3 | 100 | 0.6 | 0.4 | 0.92 | 165.6 | 36.8
1.58 OPD Info. And admitting | 3 | 150 | 0.55 | 0.45 | 0.92 | 227.7 | 62.1
1.59 OPD records |  |  |  |  | 0.92 | 0 | 0
1.60 Ultrasound | 4 | 100 | 0.6 | 0.4 | 0.92 | 220.8 | 36.8
1.64 Supply Receiving Area | 2 | 150 | 0.5 | 0.5 | 0.92 | 138 | 69
1.65 Dietician's Office | 3 | 150 | 0.55 | 0.45 | 0.92 | 227.7 | 62.1
1.66 Dietary | 3 | 100 | 0.6 | 0.4 | 0.92 | 165.6 | 36.8
1.67 Staff Dining | 8 | 100 | 0.6 | 0.4 | 0.92 | 441.6 | 36.8
1.68 OPD clinic Ob-gyne | 4 | 100 | 0.6 | 0.4 | 0.92 | 220.8 | 36.8
1.70 Canteen | 20 | 100 | 0.6 | 0.4 | 0.92 | 1104 | 36.8
SECOND FLOOR
SPACE | Occ | Gain/person | Sensible | Latent | CLF | Qs (W) | Ql (W)
5-Bed Ward 1 | 5 | 70 | 0.75 | 0.25 | 0.92 | 241.5 | 87.5
5-Bed Ward 2 | 5 | 70 | 0.75 | 0.25 | 0.92 | 241.5 | 87.5
5-Bed Ward 3 | 5 | 70 | 0.75 | 0.25 | 0.92 | 241.5 | 87.5
5-Bed Ward 4 | 5 | 70 | 0.75 | 0.25 | 0.92 | 241.5 | 87.5
Isolation Room 1 | 3 | 70 | 0.75 | 0.25 | 0.92 | 144.9 | 52.5
Private Room 1 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35
Private Room 2 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35
Chief Nurse | 4 | 100 | 0.6 | 0.4 | 0.92 | 220.8 | 160
Treatment Room | 3 | 70 | 0.75 | 0.25 | 0.92 | 144.9 | 52.5
Nurse Station | 8 | 100 | 0.6 | 0.4 | 0.92 | 441.6 | 320
Dirty Utility | 1 | 150 | 0.5 | 0.5 | 0.92 | 69 | 75
Clean Linen | 1 | 150 | 0.5 | 0.5 | 0.92 | 69 | 75
Private Room 3 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35
Private Room 4 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35
Isolation Room 2 | 3 | 70 | 0.75 | 0.25 | 0.92 | 144.9 | 52.5
Reception | 5 | 100 | 0.6 | 0.4 | 0.92 | 276 | 200
Private Room 5 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35
Chief of Hospital | 4 | 100 | 0.6 | 0.4 | 0.92 | 220.8 | 160
3-Bed Ward 1 | 3 | 70 | 0.75 | 0.25 | 0.92 | 144.9 | 52.5
3-Bed Ward 2 | 3 | 70 | 0.75 | 0.25 | 0.92 | 144.9 | 52.5
Private Room 6 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35
Conference Room | 20 | 175 | 0.5 | 0.5 | 0.92 | 1610 | 1750
3-Bed Ward 3 | 3 | 70 | 0.75 | 0.25 | 0.92 | 144.9 | 52.5
3-Bed Ward 4 | 3 | 70 | 0.75 | 0.25 | 0.92 | 144.9 | 52.5
Private Room 7 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35
Private Room 8 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 35
Chief of Clinics | 4 | 150 | 0.55 | 0.45 | 0.92 | 303.6 | 270
Delivery Room | 5 | 150 | 0.5 | 0.5 | 0.92 | 345 | 375
Sub-Ster Room 1 | 2 | 150 | 0.5 | 0.5 | 0.92 | 138 | 150
Labor Room | 3 | 150 | 0.5 | 0.5 | 0.92 | 207 | 225
Pathologic Nursery | 4 | 70 | 0.75 | 0.25 | 0.92 | 193.2 | 70
Pre-mature nursery | 10 | 70 | 0.75 | 0.25 | 0.92 | 483 | 175
Breastfeeding room | 3 | 100 | 0.6 | 0.4 | 0.92 | 165.6 | 120
Pre-operation area | 4 | 150 | 0.5 | 0.5 | 0.92 | 276 | 300
Autoclave area | 4 | 100 | 0.6 | 0.4 | 0.92 | 220.8 | 160
Sterile supply room | 2 | 100 | 0.6 | 0.4 | 0.92 | 110.4 | 80
Major Operating Room | 5 | 150 | 0.5 | 0.5 | 0.92 | 345 | 375
Sub-Ster Room 2 | 2 | 150 | 0.5 | 0.5 | 0.92 | 138 | 150
Jan.Clo. | 2 | 150 | 0.5 | 0.5 | 0.92 | 138 | 150
Clean up room | 2 | 150 | 0.5 | 0.5 | 0.92 | 138 | 150
Sterile Instrument Supply Storage Area | 5 | 100 | 0.6 | 0.4 | 0.92 | 276 | 200
Anesthesia Office & Storage | 2 | 150 | 0.55 | 0.45 | 0.92 | 151.8 | 135
Lounge Area | 3 | 150 | 0.5 | 0.5 | 0.92 | 207 | 225
Recovery Room | 3 | 70 | 0.75 | 0.25 | 0.92 | 144.9 | 52.5
THIRD FLOOR
SPACE | Occ | Gain/person | Sensible | Latent | CLF | Qs (W) | Ql (W)
5-Bed Ward 1 | 5 | 70 | 0.75 | 0.25 | 0.92 | 241.5 | 80.5
5-Bed Ward 2 | 5 | 70 | 0.75 | 0.25 | 0.92 | 241.5 | 80.5
5-Bed Ward 3 | 5 | 70 | 0.75 | 0.25 | 0.92 | 241.5 | 80.5
5-Bed Ward 4 | 5 | 70 | 0.75 | 0.25 | 0.92 | 241.5 | 80.5
Isolation Room 1 | 3 | 70 | 0.75 | 0.25 | 0.92 | 144.9 | 48.3
Private Room 1 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2
Private Room 2 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2
Chief Nurse | 4 | 150 | 0.55 | 0.45 | 0.92 | 303.6 | 248.4
Treatment Room | 3 | 100 | 0.6 | 0.4 | 0.92 | 165.6 | 110.4
Private Room 3 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2
Private Room 4 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2
Isolation Room 2 | 3 | 70 | 0.75 | 0.25 | 0.92 | 144.9 | 48.3
Private Room 5 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2
Private Room 6 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2
3-Bed Ward 1 | 3 | 70 | 0.75 | 0.25 | 0.92 | 144.9 | 48.3
3-Bed Ward 2 | 3 | 70 | 0.75 | 0.25 | 0.92 | 144.9 | 48.3
Private Room 7 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2
Private Room 8 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2
Private Room 9 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2
Private Room 10 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2
Private Room 11 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2
Private Room 12 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2
Private Room 13 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2
Private Room 14 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2
Solarium 1 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2
Solarium 2 | 2 | 70 | 0.75 | 0.25 | 0.92 | 96.6 | 32.2
Admitting | 1 | 150 | 0.55 | 0.45 | 0.92 | 75.9 | 62.1
Billing | 1 | 150 | 0.55 | 0.45 | 0.92 | 75.9 | 62.1
Cashier | 1 | 150 | 0.55 | 0.45 | 0.92 | 75.9 | 62.1
Personel's dining | 10 | 100 | 0.6 | 0.4 | 0.92 | 552 | 368

## LIGHTING LOAD
OCCUPANT LOAD
FIRST FLOOR
SPACE | W | Fu | Fb | CLF | Qs (W) | Area
1.1 Power House | 486.7018 | 0.75 | 1.2 | 0.94 | 411.7497 | 37.4386
1.2 Work Area | 125.4656 | 0.75 | 1.2 | 0.94 | 106.1439 | 9.6512
1.3 Storage Room | 101.6275 | 0.5 | 1.2 | 0.94 | 57.3179 | 7.8175
1.4 Maintenance Office | 212.0235 | 0.5 | 1.2 | 0.94 | 119.5813 | 16.3095
1.5 Female toilet | 237.8883 | 0.5 | 1.2 | 0.94 | 134.169 | 18.2991
1.6 Male Toilet | 238.5032 | 0.5 | 1.2 | 0.94 | 134.5158 | 18.3464
1.7 Minor Operating Room | 304.0518 | 0.5 | 1.2 | 0.94 | 171.4852 | 23.3886
1.8 Equipment and supply storage area | 72.93 | 0.75 | 1.2 | 0.94 | 61.6988 | 5.61
1.9 Examination/Treatment Area | 548.5025 | 0.75 | 1.2 | 0.94 | 464.0331 | 42.1925
1.10 Cadaver Holding Room | 255.2914 | 0.5 | 1.2 | 0.94 | 143.9843 | 19.6378
1.11 Supply Room | 406.7609 | 0.5 | 1.2 | 0.94 | 229.4131 | 31.2893
1.12 Bulk Storage | 51.7036 | 0.5 | 1.2 | 0.94 | 29.1608 | 3.9772
1.13 Pharmacy | 269.7331 | 0.75 | 1.2 | 0.94 | 228.1942 | 20.7487
1.14 Medical Records Office | 233.3656 | 0.75 | 1.2 | 0.94 | 197.4273 | 17.9512
1.15 Medical Records | 242.2004 | 0.75 | 1.2 | 0.94 | 204.9015 | 18.6308
1.16 PHILHEALTH | 222.7914 | 0.5 | 1.2 | 0.94 | 125.6543 | 17.1378
1.17 Doctor's Duty | 150.8806 | 0.5 | 1.2 | 0.94 | 85.0967 | 11.6062
1.18 Nurse Station (ER) | 1702.5866 | 0.75 | 1.2 | 0.94 | 1440.3883 | 130.9682
1.21 Work Area (laboratory) | 427.18 | 0.75 | 1.2 | 0.94 | 361.3943 | 32.86
1.23 Waiting area | 164.8075 | 0.75 | 1.2 | 0.94 | 139.4271 | 12.6775
1.24 OPD clinic dental 1 | 186.9543 | 0.5 | 1.2 | 0.94 | 105.4422 | 14.3811
1.25 OPD clinic dental 2 | 186.9543 | 0.5 | 1.2 | 0.94 | 105.4422 | 14.3811
1.27 OPD clinic surgery 1 | 187.6628 | 0.5 | 1.2 | 0.94 | 105.8418 | 14.4356
1.28 OPD clinic surgery 2 | 187.6628 | 0.5 | 1.2 | 0.94 | 105.8418 | 14.4356
1.29 Cashier | 71.3375 | 0.75 | 1.2 | 0.94 | 60.3515 | 5.4875
1.30 Billing | 71.63 | 0.75 | 1.2 | 0.94 | 60.599 | 5.51
1.31 Admitting | 73.2719 | 0.75 | 1.2 | 0.94 | 61.988 | 5.6363
1.32 Film File Storage | 71.7639 | 0.5 | 1.2 | 0.94 | 40.4748 | 5.5203
1.33 Radiologist Office | 118.9396 | 0.5 | 1.2 | 0.94 | 67.0819 | 9.1492
1.34 Dark Room | 64.3786 | 0.5 | 1.2 | 0.94 | 36.3095 | 4.9522
1.35 Control Booth | 328.2994 | 0.5 | 1.2 | 0.94 | 185.1609 | 25.2538
1.37 OPD Clinic Pedia 1 | 186.9543 | 0.5 | 1.2 | 0.94 | 105.4422 | 14.3811
1.38 OPD Clinic Pedia 2 | 186.9543 | 0.5 | 1.2 | 0.94 | 105.4422 | 14.3811
1.39 OPD Records | 135.434 | 0.5 | 1.2 | 0.94 | 76.3848 | 10.418
1.40 OPD info. And admitting | 129.7465 | 0.5 | 1.2 | 0.94 | 73.177 | 9.9805
1.41 OPD Clinic Medical 1 | 187.6628 | 0.5 | 1.2 | 0.94 | 105.8418 | 14.4356
1.42 OPD Clinic Medical 2 | 187.6628 | 0.5 | 1.2 | 0.94 | 105.8418 | 14.4356
1.43 Hospital Main Lobby | 8530.327 | 1 | 1.2 | 0.94 | 9622.2089 | 656.179
1.46 Pressing Area | 109.603 | 0.5 | 1.2 | 0.94 | 61.8161 | 8.431
1.47 Linen Storage | 108.0781 | 0.5 | 1.2 | 0.94 | 60.956 | 8.3137
1.49 Linen Office | 109.6875 | 0.5 | 1.2 | 0.94 | 61.8637 | 8.4375
1.50 Admin Office | 176.891 | 0.5 | 1.2 | 0.94 | 99.7665 | 13.607
1.51 Male Toilet | 224.3787 | 0.5 | 1.2 | 0.94 | 126.5496 | 17.2599
1.53 Washing Area | 222.6471 | 0.5 | 1.2 | 0.94 | 125.573 | 17.1267
1.54 Receiving Sorting Area | 111.4243 | 0.5 | 1.2 | 0.94 | 62.8433 | 8.5711
1.56 Social Welfare | 176.7792 | 0.5 | 1.2 | 0.94 | 99.7035 | 13.5984
1.57 Female Toilet | 221.5564 | 0.5 | 1.2 | 0.94 | 124.9578 | 17.0428
1.58 OPD Info. And admitting | 135.7421 | 0.5 | 1.2 | 0.94 | 76.5585 | 10.4417
1.59 OPD records | 150.6947 | 0.5 | 1.2 | 0.94 | 84.9918 | 11.5919
1.60 Ultrasound | 247.9997 | 0.5 | 1.2 | 0.94 | 139.8718 | 19.0769
1.61 Cooking Area | 444.7976 | 0.5 | 1.2 | 0.94 | 250.8658 | 34.2152
1.62 Dry storage | 33.7233 | 0.5 | 1.2 | 0.94 | 19.0199 | 2.5941
1.63 Cold Storage | 25.5125 | 0.5 | 1.2 | 0.94 | 14.389 | 1.9625
1.64 Supply Receiving Area | 74.3392 | 0.75 | 1.2 | 0.94 | 62.891 | 5.7184
1.65 Dietician's Office | 119.925 | 0.5 | 1.2 | 0.94 | 67.6377 | 9.225
1.66 Dietary | 494.4225 | 0.5 | 1.2 | 0.94 | 278.8543 | 38.0325
1.67 Staff Dining | 661.5453 | 0.75 | 1.2 | 0.94 | 559.6673 | 50.8881
1.68 OPD clinic Ob-gyne | 351.0728 | 0.5 | 1.2 | 0.94 | 198.0051 | 27.0056
1.70 Canteen | 2362.0896 | 0.5 | 1.2 | 0.94 | 1332.2185 | 181.6992
19883.6097
SECOND FLOOR
SPACE | W | Fu | Fb | CLF | Qs (W) | Area
5-Bed Ward 1 | 445.5997 | 0.75 | 1.2 | 0.94 | 376.9773 | 34.2769
5-Bed Ward 2 | 445.38 | 0.75 | 1.2 | 0.94 | 376.7915 | 34.26
5-Bed Ward 3 | 445.77 | 0.75 | 1.2 | 0.94 | 377.1214 | 34.29
5-Bed Ward 4 | 443.5275 | 0.75 | 1.2 | 0.94 | 375.2243 | 34.1175
Isolation Room 1 | 177.7594 | 0.75 | 1.2 | 0.94 | 150.3845 | 13.6738
Private Room 1 | 180.9678 | 0.75 | 1.2 | 0.94 | 153.0988 | 13.9206
Private Room 2 | 180.3802 | 0.75 | 1.2 | 0.94 | 152.6016 | 13.8754
Chief Nurse | 399.256 | 0.5 | 1.2 | 0.94 | 225.1804 | 30.712
Treatment Room | 233.2369 | 0.75 | 1.2 | 0.94 | 197.3184 | 17.9413
Nurse Station | 296.777 | 0.75 | 1.2 | 0.94 | 251.0733 | 22.829
Dirty Utility | 62.2297 | 0.5 | 1.2 | 0.94 | 35.0976 | 4.7869
Clean Linen | 31.9553 | 0.5 | 1.2 | 0.94 | 18.0228 | 2.4581
Private Room 3 | 180.3555 | 0.75 | 1.2 | 0.94 | 152.5808 | 13.8735
Private Room 4 | 180.6064 | 0.75 | 1.2 | 0.94 | 152.793 | 13.8928
Isolation Room 2 | 178.1858 | 0.75 | 1.2 | 0.94 | 150.7452 | 13.7066
Reception | 143.6786 | 0.5 | 1.2 | 0.94 | 81.0347 | 11.0522
Private Room 5 | 177.8569 | 0.75 | 1.2 | 0.94 | 150.4669 | 13.6813
Chief of Hospital | 243.5147 | 0.5 | 1.2 | 0.94 | 137.3423 | 18.7319
3-Bed Ward 1 | 329.836 | 0.75 | 1.2 | 0.94 | 279.0413 | 25.372
3-Bed Ward 2 | 331.24 | 0.75 | 1.2 | 0.94 | 280.229 | 25.48
Private Room 6 | 178.7656 | 0.75 | 1.2 | 0.94 | 151.2357 | 13.7512
Conference Room | 499.8981 | 0.5 | 1.2 | 0.94 | 281.9425 | 38.4537
3-Bed Ward 3 | 329.836 | 0.75 | 1.2 | 0.94 | 279.0413 | 25.372
3-Bed Ward 4 | 331.24 | 0.75 | 1.2 | 0.94 | 280.229 | 25.48
Private Room 7 | 178.7656 | 0.75 | 1.2 | 0.94 | 151.2357 | 13.7512
Private Room 8 | 178.7656 | 0.75 | 1.2 | 0.94 | 151.2357 | 13.7512
Chief of Clinics | 277.7008 | 0.5 | 1.2 | 0.94 | 156.6233 | 21.3616
CSSR | 408.7044 | 0.5 | 1.2 | 0.94 | 230.5093 | 31.4388
Delivery Room | 454.8206 | 0.75 | 1.2 | 0.94 | 384.7782 | 34.9862
Sub-Ster Room 1 | 70.3443 | 0.75 | 1.2 | 0.94 | 59.5113 | 5.4111
Labor Room | 334.7318 | 0.75 | 1.2 | 0.94 | 283.1831 | 25.7486
Pathologic Nursery | 218.3922 | 0.75 | 1.2 | 0.94 | 184.7598 | 16.7994
Pre-mature nursery | 218.3987 | 0.75 | 1.2 | 0.94 | 184.7653 | 16.7999
Breastfeeding room | 132.9354 | 0.5 | 1.2 | 0.94 | 74.9756 | 10.2258
Pre-operation area | 247.0091 | 0.5 | 1.2 | 0.94 | 139.3131 | 19.0007
Autoclave area | 194.8375 | 0.5 | 1.2 | 0.94 | 109.8884 | 14.9875
Sterile supply room | 280.8078 | 0.75 | 1.2 | 0.94 | 237.5634 | 21.6006
Work Area 1 | 306.8039 | 0.75 | 1.2 | 0.94 | 259.5561 | 23.6003
Major Operating Room | 455.5525 | 0.5 | 1.2 | 0.94 | 256.9316 | 35.0425
Sub-Ster Room 2 | 73.9856 | 0.75 | 1.2 | 0.94 | 62.5918 | 5.6912
Jan.Clo. | 53.7394 | 0.5 | 1.2 | 0.94 | 30.309 | 4.1338
Clean up room | 167.83 | 0.5 | 1.2 | 0.94 | 94.6561 | 12.91
Sterile instrument supply storage area | 97.2192 | 0.75 | 1.2 | 0.94 | 82.2474 | 7.4784
anesthesia office and storage | 227.7691 | 0.75 | 1.2 | 0.94 | 192.6927 | 17.5207
DR-1 | 36.4 | 0.5 | 1.2 | 0.94 | 20.5296 | 2.8
DR-2 | 36.4 | 0.5 | 1.2 | 0.94 | 20.5296 | 2.8
DR-3 | 36.4 | 0.5 | 1.2 | 0.94 | 20.5296 | 2.8
Lounge Area | 536.9273 | 0.75 | 1.2 | 0.94 | 454.2405 | 41.3021
Recovery Room | 610.6646 | 0.75 | 1.2 | 0.94 | 516.6223 | 46.9742
Hallway | #VALUE! | 0.75 | 1.2 | 0.94 | #VALUE! | 684.912+
THIRD FLOOR
SPACE | W | Fu | Fb | CLF | Qs (W) | Area
5-Bed Ward 1 | 445.5997 | 0.75 | 1.2 | 0.94 | 376.9773 | 34.2769
5-Bed Ward 2 | 445.38 | 0.75 | 1.2 | 0.94 | 376.7915 | 34.26
Waiting Area 1 | 486.3131 | 0.5 | 1.2 | 0.94 | 274.2806 | 37.4087
Waiting Area 2 | 486.3131 | 0.5 | 1.2 | 0.94 | 274.2806 | 37.4087
5-Bed Ward 3 | 445.38 | 0.75 | 1.2 | 0.94 | 376.7915 | 34.26
5-Bed Ward 4 | 445.38 | 0.75 | 1.2 | 0.94 | 376.7915 | 34.26
Isolation Room 1 | 131.8109 | 0.75 | 1.2 | 0.94 | 111.512 | 10.1393
Private Room 1 | 180.9886 | 0.75 | 1.2 | 0.94 | 153.1164 | 13.9222
Private Room 2 | 180.3594 | 0.75 | 1.2 | 0.94 | 152.5841 | 13.8738
Chief Nurse | 399.256 | 0.5 | 1.2 | 0.94 | 225.1804 | 30.712
Treatment Room | 233.2369 | 0.5 | 1.2 | 0.94 | 131.5456 | 17.9413
Nurse Station | 296.777 | 0.75 | 1.2 | 0.94 | 251.0733 | 22.829
Dirty Utility | 62.2297 | 0.5 | 1.2 | 0.94 | 35.0976 | 4.7869
Clean Linen | 31.9553 | 0.5 | 1.2 | 0.94 | 18.0228 | 2.4581
Private Room 3 | 180.3555 | 0.75 | 1.2 | 0.94 | 152.5808 | 13.8735
Private Room 4 | 180.6064 | 0.75 | 1.2 | 0.94 | 152.793 | 13.8928
Isolation Room 2 | 132.2308 | 0.75 | 1.2 | 0.94 | 111.8673 | 10.1716
Private Room 5 | 206.2047 | 0.75 | 1.2 | 0.94 | 174.4492 | 15.8619
Privaate Room 6 | 206.2047 | 0.75 | 1.2 | 0.94 | 174.4492 | 15.8619
3-Bed Ward 1 | 322.179 | 0.75 | 1.2 | 0.94 | 272.5634 | 24.783
3-Bed Ward 2 | 323.5817 | 0.75 | 1.2 | 0.94 | 273.7501 | 24.8909
Private Room 7 | 177.8569 | 0.75 | 1.2 | 0.94 | 150.4669 | 13.6813
Private Room 8 | 178.7656 | 0.75 | 1.2 | 0.94 | 151.2357 | 13.7512
Private Room 9 | 208.1456 | 0.75 | 1.2 | 0.94 | 176.0912 | 16.0112
Private Room 10 | 208.1456 | 0.75 | 1.2 | 0.94 | 176.0912 | 16.0112
Private Room 11 | 178.7656 | 0.75 | 1.2 | 0.94 | 151.2357 | 13.7512
Private Room 12 | 178.7656 | 0.75 | 1.2 | 0.94 | 151.2357 | 13.7512
Waiting Area | 305.2777 | 0.75 | 1.2 | 0.94 | 258.2649 | 23.4829
Private Room 13 | 139.8436 | 0.75 | 1.2 | 0.94 | 118.3077 | 10.7572
Private Room 14 | 147.095 | 0.75 | 1.2 | 0.94 | 124.4424 | 11.315
Solarium 1 | 173.0079 | 0.5 | 1.2 | 0.94 | 97.5765 | 13.3083
Stretcher's Wheelchair Nook 1 | 144.1336 | 1 | 1.2 | 0.94 | 162.5827 | 11.0872
Stretcher's Wheelchair Nook 2 | 107.575 | 1 | 1.2 | 0.94 | 121.3446 | 8.275
Solarium 2 | 175.0775 | 0.5 | 1.2 | 0.94 | 98.7437 | 13.4675
Water Tank | 2391.2694 | 0.75 | 1.2 | 0.94 | 2023.0139 | 183.9438
Chapel | 765.1813 | 1 | 1.2 | 0.94 | 863.1245 | 58.8601
Male Toilet | 226.7876 | 0.75 | 1.2 | 0.94 | 191.8623 | 17.4452
Female Toilet | 227.2478 | 0.75 | 1.2 | 0.94 | 192.2516 | 17.4806
Waiting Area | 566.6882 | 0.5 | 1.2 | 0.94 | 319.6121 | 43.5914
Admitting | 141.7078 | 0.75 | 1.2 | 0.94 | 119.8848 | 10.9006
Billing | 140.1803 | 0.75 | 1.2 | 0.94 | 118.5925 | 10.7831
Cashier | 122.4119 | 0.75 | 1.2 | 0.94 | 103.5605 | 9.4163
Personel's dining | 350.9454 | 0.75 | 1.2 | 0.94 | 296.8998 | 26.9958
Hospital main lobby |  | 1 | 1.2 | 0.94 | 0 | 628.02+

## References
Reference |  |  |  |  | Awning or Sliding | 2.8722
First Floor |  |  |  |  | Fixed | 2.8211 | References |  | Ground |  | Second | Third
Walls | [6 empty] | Daily Range | 8.1 | no. of changes/hr | Area (m2) | Area | no.of changes/hr | Area (m2)
Length | Area |  | Width | Length |  |  | Tdb | 34.5 | 0.264 | 37.4386 | 34.2769 | 0.264 | 34.2769
4 | 4 |  | 2 | 1 |  |  |  |  | 0.264 | 9.6512 | 2.6175 | 0.2535 | 2.6175
| 0 |  | 1.2 | 1 |  |  |  |  | 0.2535 | 7.8175 | 34.26 | 0.264 | 34.26
1.2 | 1.2 |  | 0.6 | 0.6 |  |  |  |  | 0.264 | 16.3095 | 2.6175 | 0.264 | 2.6175
0.6 | 0.36 |  | 1.2 | 0.6 |  |  |  |  | 0.2535 | 2.8375 | 220.3324 | 0.264 | 37.4087
1.2 | 0.72 |  | 1.2 | 0.6 |  |  |  |  | 0.2535 | 18.2991 | 143.2911 | 0.264 | 37.4087
1.2 | 0.72 |  | 1.6 | 1 |  |  |  |  | 0.2535 | 18.3464 | 78.7574 | 0.264 | 34.26
1.6 | 1.6 |  | 2.2 | 1 |  |  |  |  | 0.2675 | 23.3886 | 99.6547 | 0.2535 | 2.6175
4.4 | 4.4 |  | 1.2 | 0.6 |  |  |  |  | 0.2535 | 5.61 | 142.8801 | 0.264 | 34.26
| 0 |  | 2 | 1 |  |  |  |  | 0.264 | 42.1925 | 34.29 | 0.2535 | 2.6175
1.2 | 0.72 |  | 2.75 | 1 |  |  |  |  | 0.2535 | 3.7087 | 2.6175 | 0.264 | 10.1393
1.6 | 1.6 |  | 3.6 | 2.5 |  |  |  |  | 0.264 | 19.6378 | 34.1175 | 0.2535 | 2.6222
4.4 | 4.4 |  | 0.6 | 1 |  |  |  |  | 0.264 | 31.2893 | 2.6175 | 0.264 | 13.9222
8.15 | 8.15 |  | 4.2 | 1 |  |  |  |  | 0.2535 | 3.9772 | 13.6738 | 0.2535 | 2.6155
2.4 | 2.4 |  | 0.6 | 0.6 |  |  |  |  | 0.264 | 20.7487 | 2.6231 | 0.264 | 13.8738
0.6 | 0.36 |  | 0.6 | 1 |  |  |  |  | 0.264 | 17.9512 | 13.9206 | 0.2535 | 2.6186
0.6 | 0.36 |  | 1.6 | 1 |  |  |  |  | 0.264 | 18.6308 | 2.6155 | 0.264 | 30.712
2 | 2 |  | 0.6 | 0.6 |  |  |  |  | 0.264 | 17.1378 | 13.8754 | 0.2535 | 2.6374
4.8 | 4.8 |  | 4.2 | 1 |  |  |  |  | 0.264 | 11.6062 | 2.6197 | 0.264 | 17.9413
0.6 | 0.36 |  | 8.4 | 1 |  |  |  |  | 0.264 | 130.9682 | 30.712 | 0.264 | 22.829
| 0 |  | 1.4 | 1 |  |  |  |  | 0.2535 | 2.9773 | 2.6374 | 0.2535 | 2.415
4.2 | 4.2 |  | 2.4 | 1 |  |  |  |  | 0.264 | 656.179 | 17.9413 | 0.2535 | 4.7869
2.8 | 2.8 |  | 2.8 | 1 |  |  |  |  | 0.2675 | 32.86 | 22.829 | 0.2535 | 2.4581
2.8 | 1.68 |  | 1.8 | 1 |  |  |  |  | 0.264 | 12.6775 | 2.4121 | 0.264 | 13.8735
2.4 | 2.4 |  | 2.4 | 1 |  |  |  |  | 0.2535 | 3.2363 | 4.7869 | 0.2535 | 2.6175
| 0 |  | 1.73 | 1 |  |  |  |  | 0.264 | 14.3811 | 2.4581 | 0.264 | 13.8928
2.2 | 2.2 |  | 2 | 1 |  |  |  |  | 0.264 | 14.3811 | 13.8735 | 0.2535 | 2.6175
| 0 |  | 0.6 | 0.6 |  |  |  |  | 0.264 | 8.9651 | 2.6175 | 0.264 | 10.1716
0.6 | 0.36 |  | 0.6 | 0.6 |  |  |  |  | 0.264 | 14.4356 | 13.8928 | 0.2535 | 2.6213
| 0 |  | 2.4 | 1 |  |  |  |  | 0.264 | 14.4356 | 2.6175 | 0.264 | 15.8619
| 0 |  | 1.6 | 1 |  |  |  |  | 0.264 | 5.4875 | 13.7066 | 0.2535 | 2.64
14 | 14 | [7 empty] | 0.264 | 5.51 | 2.6213 | 0.264 | 15.8619
| 0 | [7 empty] | 0.264 | 5.6363 | 11.0522 | 0.2535 | 2.64
[9 empty] | 0.2535 | 5.5203 | 13.6813 | 0.264 | 24.783
Third Floor | [8 empty] | 0.264 | 9.1492 | 2.64 | 0.2535 | 2.64
Wall | [8 empty] | 0.264 | 4.9522 | 18.7319 | 0.264 | 24.8909
Doors | Windows | Wall Length | Width | Length |  |  |  |  | 0.264 | 25.2538 | 6.9296 | 0.2535 | 2.64
0 | 0 | 6.5 | 2.31 | 1 |  |  |  |  | 0.264 | 14.3811 | 25.372 | 0.264 | 13.6813
0 | 4.6 | 6 | 2.31 | 1 |  |  |  |  | 0.264 | 14.3811 | 2.6087 | 0.2535 | 2.64
0 | 4.6 | 6 | 2.31 | 1 |  |  |  |  | 0.264 | 10.418 | 6.6151 | 0.264 | 13.7512
0 | 0 | 10.23 | 2.31 | 1 |  |  |  |  | 0.264 | 9.9805 | 25.48 | 0.2535 | 2.64
0 | 0 | 17 | 2.7 | 1 |  |  |  |  | 0.264 | 14.4356 | 2.6087 | 0.264 | 16.0112
0 | 0 | 10.23 | 1.4 | 1 |  |  |  |  | 0.264 | 14.4356 | 13.7512 | 0.2535 | 2.64
0 | 4.6 | 6 | 1.4 | 1 |  |  |  |  | 0.264 | 14.3639 | 2.64 | 0.264 | 16.0112
0 | 4.6 | 6 | 1.4 | 1 |  |  |  |  | 0.264 | 8.431 | 38.4537 | 0.2535 | 2.64
0 | 0 | 6.5 | 1.4 | 1 |  |  |  |  | 0.2535 | 8.3137 | 25.372 | 0.264 | 8.9651
0 | 2.7 | 3.1 | 1.4 | 1 |  |  |  |  | 0.264 | 8.4375 | 2.6087 | 0.264 | 13.7512
0 | 1.4 | 3.7 | 3.35 | 1 |  |  |  |  | 0.264 | 13.607 | 25.48 | 0.2535 | 2.64
0 | 1.4 | 2.35 | 2.4 | 1 |  |  |  |  | 0.2535 | 17.2599 | 2.6087 | 0.264 | 13.7512
0 | 0 | 3 | 2.4 | 1 |  |  |  |  | 0.264 | 17.1267 | 13.7512 | 0.2535 | 2.64
0 | 1.4 | 3 | 2.4 | 1 |  |  |  |  | 0.264 | 8.5711 | 2.64 | 0.264 | 23.4829
0 | 1.4 | 3 | 2.23 | 1 |  |  |  |  | 0.264 | 35.3177 | 13.7512 | 0.264 | 10.7572
0 | 1.4 | 3 | 0.6 | 0.6 |  |  |  |  | 0.264 | 13.5984 | 2.64 | 0.2535 | 2.64
0 | 1.4 | 3 | 2.4 | 1 |  |  |  |  | 0.2535 | 17.0428 | 21.3616 | 0.264 | 11.315
0 | 3.35 | 3.75 | 1.2 | 0.6 |  |  |  |  | 0.264 | 10.4417 | 1.6646 | 0.2535 | 2.64
0 | 0 | 3 | 1.2 | 0.6 |  |  |  |  | 0.264 | 11.5919 | 31.4388 | 0.264 | 13.3083
0 | 2.4 | 3.9 | [6 empty] | 0.264 | 19.0769 | 34.9862 | 0.264 | 11.0872
0 | 2.4 | 3.9 | 3.35 | 1 |  |  |  |  | 0.2535 | 2.5344 | 5.4111 | 0.264 | 8.275
0 | 2.4 | 3.2 | 1.4 | 1 |  |  |  |  | 0.2535 | 34.2152 | 25.7486 | 0.264 | 13.4675
0 | 2.23 | 2.48 | 1.4 | 1 |  |  |  |  | 0.2535 | 2.5941 | 3.863 | 0.264 | 183.9438
0 | 0.6 | 1.88 | 1.4 | 1 |  |  |  |  | 0.2535 | 1.9625 | 16.7994 | 0.264 | 58.8601
0 | 0.6 | 1.5 | 1.4 | 1 |  |  |  |  | 0.264 | 5.7184 | 16.7999 | 0.2535 | 17.4452
0 | 2.4 | 5.7 | 1.4 | 1 |  |  |  |  | 0.264 | 9.225 | 10.2258 | 0.2535 | 17.4806
0 | 0 | 4.8 | 0.6 | 0.6 |  |  |  |  | 0.2535 | 1.945 | 19.0007 | 0.264 | 43.5914
0 | 1.2 | 3 | [6 empty] | 0.264 | 38.0325 | 14.9875 | 0.264 | 10.9006
0 | 1.2 | 3 | [6 empty] | 0.264 | 50.8881 | 1.68 | 0.264 | 10.7831
0 |  | 6 | [6 empty] | 0.264 | 27.0056 | 21.6006 | 0.264 | 9.4163
0 | 0 | 12 | [6 empty] | 0.2535 | 2.5344 | 23.6003 | 0.264 | 26.9958
0 | 0 | 15.4 | [6 empty] | 0.264 | 2.28 | 35.0425 | 0.2535 | 2.64
0 | 0 | 2.22 | [6 empty] | 0.2535 | 181.6992 | 5.6912 | 0.264 | 628.0183
0 | 3.33 | 3.75 | [8 empty] | 4.1338
0 | 1.4 | 3 | [8 empty] | 12.91
0 | 1.4 | 3 | [8 empty] | 7.4784
0 | 1.4 | 3 | [8 empty] | 17.5207
0 | 1.4 | 3 | [8 empty] | 2.8
0 | 0 | 2.22 | [8 empty] | 2.8
0 | 1.4 | 3.7 | [8 empty] | 2.8
0 | 0.6 | 2.35 | [8 empty] | 41.3021
5 | 0 | 3.1 | [8 empty] | 46.9742
2.0901
Note on E60: Adrian: Hallway