## GROUND
GROUND FLOOR | ELEC. EQ. RATING | Inside (Tdb) | No. of occ. | Vent. Rate | Gain/person | SHG | LHG | Lamp Rating (W) | Area/Room
Maintenance office | CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 25 | 3 | 7.5 | 100 | 60 | 40 | 32 | 17.0113
Minor operating room | SMOKE DETECTOR, 0.4W CARDIOPULMONARY BYPASS MACHINE, 150 W SURGICAL LGHTS, 25W AUTOCLAVE, 2000W | 22 | 6 | 75 | 150 | 50 | 50 |  | 24.7
Examination/Treament/Observation area | CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 25 | 6 | 48 | 100 | 60 | 40 |  | 43.65
Supply Room | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 25 | 2 | 32 | 100 | 60 | 40 | 32 | 35.5475
Pharmacy | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 25 | 4 | 32 | 100 | 60 | 40 | 32 | 27.1125
Medical records office | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 25 | 2 | 7.5 | 100 | 60 | 40 | 32 | 18.075
Philhealth | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 25 | 5 | 7.5 | 150 | 50 | 50 | 32 | 18.075
Doctors on duty | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 25 | 4 | 10 | 150 | 50 | 50 | 32 | 14.9362
Emergency room | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 24 | 6 | 48 | 150 | 50 | 50 |  | 54.225
Patho office | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 22 | 4 | 32 | 100 | 60 | 40 | 32
Radiologist office | TV, 125W- TELEPHONE, 5W SMOKE DETECTOR, 1.6W CEILING ORBITAL FAN, 70W | 22 | 5 | 24 | 100 | 60 | 40 | 32
X-ray Room | X-RAY MACHINE, 1500W SMOKE DETECTOR, 0.8W | 25 | 4 | 32 | 150 | 50 | 50
OPD clinic (8) | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 25 | 8 | 10 | 150 | 50 | 50 | 32 | 14.625
OPD info and admitting - a | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 25 | 3 | 7.5 | 150 | 55 | 45 | 32 | 7.3125
Cashier | TV, 125W TELEPHONE, 5W CASH REGISTER, 100W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 25 | 1 | 7.5 | 150 | 55 | 45 | 32 | 6
Billing | TV, 125W TELEPHONE, 5W CASH REGISTER, 100W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 25 | 1 | 7.5 | 150 | 55 | 45 | 32 | 6
Admitting | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 25 | 1 | 7.5 | 150 | 50 | 50 | 32 | 6
Administrative Office | TELEPHONE, 5W TV, 125W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 25 | 2 | 7.5 | 150 | 50 | 50 | 32 | 36.6
Admin Office | TELEPHONE, 5W TV, 125W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 25 | 2 | 7.5 | 150 | 50 | 50 | 32 | 18.3
Social Welfare | TELEPHONE, 5W TV, 125W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 25 | 3 | 7.5 | 150 | 50 | 50 | 32 | 18.3
OPD info and admitting - b | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 25 | 3 | 7.5 | 150 | 55 | 45 | 32 | 11.7375
Ultrasound | TV, 150W TELEPHONE, 5W ULTRASOUND MACHINE, 95W SMOKE DETECTOR, 0.4W | 24 | 4 | 32 | 100 | 60 | 40 |  | 20.3362
OPD ob-gyne | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 24 | 4 | 24 | 100 | 60 | 40 | 32 | 28.3612
Canteen | TV, 150W TELEPHONE, 5W SMOKE DETECTOR, 1.2W CEILING ORBITAL FAN, 70W EXHAUST FAN, 40W | 25 | 20 | 160 | 100 | 60 | 40 | 32 | 189.6
Dietitians office | TV, 150W TELEPHONE, 5W SMOKE DETECTOR, 0.4W | 25 | 3 | 7.5 | 100 | 50 | 40 | 32
dry storage | SMOKE DETECTOR, 0.4W | 25 | 5 | 40 | 100 | 50 | 40 | 32
cold storage | SMOKE DETECTOR, 0.4W | 25 | 5 | 40 | 100 | 50 | 40 | 32
Supply recieving area | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 25 | 2 | 32 | 100 | 50 | 40 | 32
Cadaver Holding Room | SMOKE DETECTOR, 0.4W

## SECOND
SECOND FLOOR | ELEC. EQ. RATING | Inside (Tdb) | No. of occ. | Vent. Rate | Gain/person | SHG | LHG | Lamp Rating (W) | Area/Room
5 Bed ward (4) | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25 | 10 | 65 | 70 | 75 | 25 | 32 | 35.8612
Isolation room (2) | SMOKE DETECTOR, 0.4W TELEPHONE, 5W | 24 | 5 | 65 | 70 | 75 | 25
Private room (4) - a | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 125 W MINIFRIDGE,100W | 25 | 3 | 52 | 70 | 75 | 25 | 32 | 14.9362
Chief nurse | SMOKE DETECTOR, 0.4W TELEPHONE, 5W COMPUTER, 80W | 25 | 4 | 10 | 100 | 60 | 40 | 32 | 33.0112
Treatment room | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 24 | 5 | 12.5 | 70 | 75 | 25 |  | 18.5
Reception | SMOKE DETECTOR, 0.4W TELEPHONE, 5W COMPUTER, 80W | 25 | 8 | 65 | 100 | 60 | 40 | 32
Private room (4) - b | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 125 W MINIFRIDGE,0.66W | 25 | 3 | 52 | 70 | 75 | 25 | 32 | 14.8613
3 Bed ward (4) | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25 | 6 | 65 | 70 | 75 | 25 | 32 | 26.1112
Conference room | TELEPHONE, 5W TV, 125 W COMPUTER, 80W WATER DISPENSER 600W | 25 | 5 | 12.5 | 100 | 60 | 40 | 32 | 40.65
Chief of clinics | SMOKE DETECTOR, 0.4W TELEPHONE, 5W COMPUTER, 80W | 25 | 4 | 10 | 100 | 60 | 40 | 32
Delivery room | SMOKE DETECTOR, 0.8W | 22 | 5 | 40 | 150 | 50 | 50 |  | 33.4612
Sub-ster room (2) | SMOKE DETECTOR, 0.4W | 25 | 4 | 10 | 100 | 60 | 40 | 32 | 5.8219
Major operating room | SMOKE DETECTOR, 0.4W CARDIOPULMONARY BYPASS MACHINE, 150 W SURGICAL LGHTS, 25W AUTOCLAVE, 1400W | 22 | 8 | 75 | 150 | 50 | 50 |  | 36.6
Labor room | SMOKE DETECTOR, 0.4W SMOKE DETECTOR, 0.8W SPEAKER, 4W FIRE ALARM, 1W | 22 | 5 | 40 | 150 | 50 | 50 |  | 25.1625
Pathologic nursery | SMOKE DETECTOR, 0.4W | 24 | 4 | 32 | 100 | 60 | 40 | 32 | 18.875
Pre-mature nursery | SMOKE DETECTOR, 0.4W INCUBATOR 100W | 24 | 4 | 32 | 100 | 60 | 40 | 32 | 18.875
Breastfeeding room | SMOKE DETECTOR, 0.4W | 25 | 3 | 7.5 | 100 | 60 | 40 | 32 | 10.57
Pre-operation area | SMOKE DETECTOR, 0.4W SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 24 | 4 | 32 | 100 | 60 | 40 |  | 19.52
CSSR | TELEPHONE, 5W TV, 150 W SMOKE DETECTOR, 0.8W AUTOCLAVE, 1400W FRIDGE 200W | 25 | 7 | 56 | 100 | 60 | 40 | 32 | 47.4263
Sterile supply room | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 24 | 7 | 56 | 100 | 60 | 40 | 32 | 23.475
recovery room | SMOKE DETECTOR, 0.4W | 25 | 5 | 40 | 70 | 75 | 25 |  | 48.9375
DR (3) | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 25 | 4 | 10 | 100 | 60 | 40
Anesthesia office | TELEPHONE, 5W SMOKE DETECTOR, 0.4W | 25 | 2 | 5 | 100 | 60 | 40 | 32
Sterile instrument supply storage area | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 24 | 7 | 56 | 100 | 60 | 40 | 32

## THIRD
THIRD FLOOR | ELEC. EQ. RATING | Inside (Tdb) | No. of Occ. | Vent. Rate | Gain/person | SHG | LHG | Lamp Rating (W) | ELEC. EQ. RATING
5 Bed ward (4) | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25 | 10 | 65 | 70 | 75 | 25 | 32
Isolation room (2) | SMOKE DETECTOR, 0.4W TELEPHONE, 5W | 24 | 5 | 65 | 70 | 75 | 25
Private Room (4) - a | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 25 | 3 | 52 | 70 | 75 | 25 | 32
Chief nurse | SMOKE DETECTOR, 0.4W TELEPHONE, 5W COMPUTER, 225W | 25 | 4 | 10 | 100 | 60 | 40 | 32
Treatment room | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 24 | 5 | 12.5 | 70 | 75 | 25
Private Room (8) - b | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 25 | 3 | 52 | 70 | 75 | 25 | 32
3 Bed ward (2) | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 25 | 6 | 65 | 70 | 75 | 25 | 32
Private Room (4) - c | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 25 | 3 | 52 | 70 | 75 | 25 | 32
4 Bed ward (4) | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 25 | 8 | 65 | 70 | 75 | 25 | 32
Personnels Dining | SMOKE DETECTOR, 0.4W Fridge, 150W WATER DISPENSER 600W Oven 1200W | 25 | 10 | 65 | 100 | 60 | 40 | 32

## FOURTH
FOURTH FLOOR | ELEC. EQ. RATING | Inside (Tdb) | No. of Occ. | Vent. Rate | Gain/person | SHG | LHG | Lamp Rating (W) | ELEC. EQ. RATING | Area/Room
5 Bed ward (4) - a | SMOKEDETECTOR,0.4W CEILING ORBITAL FAN, 70W | 25 | 10 | 65 | 70 | 75 | 25 | 32 |  | 36.1863
Isolation room (2) - a | SMOKE DETECTOR, 0.4W TELEPHONE, 5W | 24 | 5 | 65 | 70 | 75 | 25 |  |  | 20.3362
5 Bed ward (4) - b | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 25 | 10 | 65 | 70 | 75 | 25 | 32
Treatment Room | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 24 | 5 | 12.5 | 70 | 75 | 25
5 Bed ward (2) - c | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 25 | 10 | 65 | 70 | 75 | 25 | 32
5 Bed ward (3) - d | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 25 | 10 | 65 | 70 | 75 | 25 | 32
3 bed ward (4) - a | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 25 | 6 | 65 | 70 | 75 | 25 | 32
4 bed ward (5) | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 25 | 8 | 65 | 70 | 75 | 25 | 32
Private room | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 25 | 3 | 52 | 70 | 75 | 25 | 32
3 bed ward (2) - b | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 25 | 6 | 65 | 70 | 75 | 25 | 32
6 bed ward | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 25 | 12 | 65 | 70 | 75 | 25 | 32
Isolation room - b | SMOKE DETECTOR, 0.4W TELEPHONE, 5W | 24 | 5 | 65 | 70 | 75 | 25

## FIFTH
FIFTH FLOOR | ELEC. EQ. RATING | Inside (Tdb) | No. of Occ. | Vent. Rate | Gain/person | SHG | LHG | Lamp Rating (W)
Private room (8) - a | SMOKE DETECTOR, 0.4W TELEPHONE, 15W TV, 150 W MINIFRIDGE,0.66W | 25 | 3 | 52 | 70 | 75 | 25 | 32
Isolation room (2) - a | SMOKE DETECTOR, 0.4W TELEPHONE, 15W | 24 | 5 | 65 | 70 | 75 | 25
Private room (4) - b | SMOKE DETECTOR, 0.4W TELEPHONE, 15W TV, 150 W MINIFRIDGE,0.66W | 25 | 3 | 52 | 70 | 75 | 25 | 32
Chief nurse | SMOKE DETECTOR, 0.4W TELEPHONE, 15W COMPUTER, 225W | 25 | 4 | 10 | 100 | 60 | 40 | 32
Treatment room a | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 24 | 5 | 12.5 | 70 | 75 | 25
Private room (4) - c | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 50 W MINIFRIDGE,0.66W | 25 | 3 | 52 | 70 | 75 | 25 | 32
Private room (4) - d | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 125 W MINIFRIDGE,0.66W | 25 | 3 | 52 | 70 | 75 | 25 | 32
Private room (8) - e | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 25 | 3 | 52 | 70 | 75 | 25 | 32
Private room (5) - f | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 25 | 3 | 52 | 70 | 75 | 25 | 32
Treatment room b | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 24 | 5 | 12.5 | 70 | 75 | 25
Private room (3) - g | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 25 | 3 | 52 | 70 | 75 | 25 | 32