## Sheet1
SUMMARY OF HEAT LOAD CALCULATION FOR GROUND FLOOR AT 22 °C |  |  | SUMMARY OF HEAT LOAD CALCULATION FOR GROUND FLOOR AT 28 °C
HEAT SOURCES | Qs (W) | Ql (W) | HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 1945.6819 | 0 | External Wall | 4465.324 | 0
Glass Load | 962.044 | 0 | Glass Load | 3846.361 | 0
Infiltration Load | 257.4623 | 497.3868 | Infiltration Load | 0 | 0
Ventilation Load | 1309 | 2528.833 | Ventilation Load | 2845.6121 | 3649.7103
Lighting Load | 532.8795 | 0 | Lighting Load | 9622.209 | 0
Occupant Load | 483 | 138 | Occupant Load | 0 | 0
Wall Partition Load | 796.785 | 0 | Wall Partition Load | 0 | 0
Door Partition Load | 5.894 | 0 | Door Partition Load |  | 0
Miscellaneous Load | 723.6979 | 365.504 | Miscellaneous Load | 19.5782 | 9.888
TOTAL | 7016.4446 | 3529.7238 | TOTAL | 20799.0843 | 3659.5983
OVERALL TOTAL | 10546.1684 |  | OVERALL TOTAL | 24458.6826
SUMMARY OF HEAT LOAD CALCULATION FOR GROUND FLOOR AT 22.5°C
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 16186.7272 | 0
Glass Load | 6662.6442 | 0
Infiltration Load | 3885.6216 | 7455.7825
Ventilation Load | 5884.032 | 11457.0125
Lighting Load | 7216.6545 | 0
Occupant Load | 4845.18 | 1713.96
Wall Partition Load | 14155.42 | 0
Door Partition Load | 1130.043 | 0
Miscellaneous Load | 380.2043 | 1920.224
TOTAL | 60346.5268 | 22546.979
OVERALL TOTAL | 82893.5058
SUMMARY OF HEAT LOAD CALCULATION FOR GROUND FLOOR AT 24°C
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 16630.0345 | 0
Glass Load | 5175.5414 | 0
Infiltration Load | 1180.8 | 2558.912
Ventilation Load | 2069.76 | 4244.8882
Lighting Load | 2511.867 | 0
Occupant Load | 1104 | 36.8
Wall Partition Load | 3602.335 | 0
Door Partition Load | 11.986 | 0
Miscellaneous Load | 901.9296 | 455.52
TOTAL | 33188.2535 | 7296.1202
OVERALL TOTAL | 40484.3736

## Sheet2
SUMMARY OF HEAT LOAD CALCULATION FOR SECOND FLOOR AT 22 °C |  |  | SUMMARY OF HEAT LOAD CALCULATION FOR GROUND FLOOR AT 28 °C
HEAT SOURCES | Qs (W) | Ql (W) | HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 2286.793 | ___ | External Wall | 4211.4145 | 0
Glass Load | 0 | ___ | Glass Load | 883.6348 | 0
Infiltration Load | 406.8458 | 787.2558 | Infiltration Load | 2663.3 | 3421.44
Ventilation Load | 3757.6 | 7259.237 | Ventilation Load | 0 | 0
Lighting Load | 641.7098 | 0 | Lighting Load | 7532.714 | 0
Occupant Load | 3867 | 1500 | Occupant Load | 0
Wall Partition Load | 1935.096 | 0 | Wall Partition Load | 0 | 0
Door Partition Load | 110 | 0 | Door Partition Load |  | 0
Miscellaneous Load | 1474.1337 | 744.512 | Miscellaneous Load | 14.5094 | 7.328
TOTAL | 14479.1783 | 10291.0048 | TOTAL | 15305.5728 | 3428.768
OVERALL TOTAL | 24770.1831 |  | OVERALL TOTAL | 18734.3408
SUMMARY OF HEAT LOAD CALCULATION FOR SECOND FLOOR AT 22.5°C
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 18499.33 | 0
Glass Load | 11264.605 | 0
Infiltration Load | 3339.8875 | 6560.8163
Ventilation Load | 15796.7 | 30952.7564
Lighting Load | 8698.5097 | 0
Occupant Load | 3959.9 | 4052.5
Wall Partition | 15295 | 0
Door Partition | 1021.7438 | 0
Miscellaneous Load | 1927.9424 | 973.6448
TOTAL | 79803.6184 | 42539.7175
OVERALL TOTAL | 122343.3359
SUMMARY OF HEAT LOAD CALCULATION FOR SECOND FLOOR AT 24°C
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 4579.7525 | 0
Glass Load | 2949.2208 | 0
Infiltration Load | 577.8417 | 1187.028
Ventilation Load | 614.46 | 1260.2016
Lighting Load | 524.0859 | 0
Occupant Load | 938.4 | 880
Wall Partition Load | 2660.492 | 0
Door Partition Load | 98.0762 | 0
Miscellaneous Load | 68.3654 | 34.528
TOTAL | 13010.6945 | 3361.7576
OVERALL TOTAL | 16372.4521

## Sheet3
SUMMARY OF HEAT LOAD CALCULATION FOR THIRD FLOOR AT 22 °C |  |  | SUMMARY OF HEAT LOAD CALCULATION FORTHIRD FLOOR AT 28 °C
HEAT SOURCES | Qs (W) | Ql (W) | HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 0 | ___ | External Wall | 12290.4232 | 0
Glass Load | 0 | ___ | Glass Load | 884.5316 | 0
Infiltration Load | 0 | 0 | Infiltration Load | 1612.958 | 3819.211
Ventilation Load | 0 | 0 | Ventilation Load | 0 | 0
Lighting Load | 0 | 0 | Lighting Load | 13863.65 | 0
Occupant Load | 0 |  | Occupant Load | 0 | 0
Partition Load | 0 |  | Wall Partition Load | 0 | 0
Miscellaneous Load | 0 |  | Door Partition Load |  | 0
|  |  | Miscellaneous Load | 30.4001 | 15.3536
TOTAL | 0
OVERALL TOTAL | 0 |  | TOTAL | 28681.9629 | 3834.5646
|  |  | OVERALL TOTAL | 32516.5275
SUMMARY OF HEAT LOAD CALCULATION FOR THIRD FLOOR AT 22.5°C
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 24827.8839 | 0
Roof Load | 27420.0353 | 0
Glass Load | 11472.723 | 0
Infiltration Load | 2478.2697 | 5099.3607
Ventilation Load | 13106.018 | 26381.3026
Lighting Load | 6378.502 | 0
Occupant Load | 4519.5 | 2132.1
Wall Partition Load | 11615.785 | 0
Door Partition Load | 1000.6511 | 0
Miscellaneous Load | 2157.1739 | 1089.4816
TOTAL | 104976.5419 | 34702.2449
OVERALL TOTAL | 139678.7868
SUMMARY OF HEAT LOAD CALCULATION FOR THIRD FLOOR AT 24°C
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 11065.523 | 0
Roof Load | 5910.7248 | 0
Glass Load | 436.0549 | 0
Infiltration Load | 1170.876 | 2401.36
Ventilation Load | 620.928 | 1273.4662
Lighting Load | 2460.248 | 0
Occupant Load | 0 | 0
Wall Partition Load | 3266.075 | 0
Door Partition Load | 67.8989 | 0
Miscellaneous Load | 0 | 0
TOTAL | 24998.3287 | 3674.8262
OVERALL TOTAL | 28673.1549