## EXTERNAL WALL LOAD
EXTERNAL WALL LOAD
FIRST FLOOR
Space | Orientation | U | A(m^2) | CLTDsel | LM | k | Ti | Tave | CLTD adj | Q(W)
Power House | E | 2.7144 | 22 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 1492.92
Power House | N | 2.7144 | 16 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 564.5952
Maintenance Office | N | 2.7144 | 5.8 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 204.6658
Maintenance Office CR | N | 2.7144 | 5.04 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 177.8475
Female Toilet | N | 2.7144 | 11.28 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 398.0396
Male Toilet | N | 2.7144 | 11.28 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 398.0396
MINOR OPERATING ROOM | N | 2.7144 | 13.6 | 13 | 2.22 | 0.65 | 22 | 30.45 | 14.343 | 479.9059
Examination/Treatment AREA | N | 2.7144 | 19.6 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 691.6291
Examination/Treatment AREA | W | 2.7144 | 29.6 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 2651.4259
CR | N | 2.7144 | 8.08 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 285.1206
Cadaver Holding Room | E | 2.7144 | 22.4 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 1520.064
EMERGENCY ROOM | W | 2.7144 | 23.6 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 2113.9747
HALLWAY | W | 2.7144 | 49.85 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 4465.3237
Work Area (laboratory) | E | 2.7144 | 21.6 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 1465.776
WAITING AREA (CR) | E | 2.7144 | 6.12 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 415.3032
Film File Storage | E | 2.7144 | 6.04 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 409.8744
Pressing Area | E | 2.7144 | 10 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 678.6
Ultrasound | N | 2.7144 | 5.24 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 184.9049
Ultrasound | W | 2.7144 | 19.2 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 1719.8438
Ultrasound CR | N | 2.7144 | 6.4 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 225.8381
Ultrasound CR | W | 2.7144 | 7.04 | 33 | -0.55 | 0.65 | 24 | 30.45 | 23.5425 | 630.6094
Cooking Area | S | 2.7144 | 12.52 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 747.6543
Cooking Area | E | 2.7144 | 19.8 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 1343.628
Dietician's Office | S | 2.7144 | 11.6 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 692.7149
Dietician's Office CR | S | 2.7144 | 5.6 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 334.4141
Staff Dining | S | 2.7144 | 26.12 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 1559.8028
OPD clinic Ob-gyne | W | 2.7144 | 10.64 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 953.0801
OPD clinic Ob-gyne | S | 2.7144 | 19.4 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 1158.5059
CR | W | 2.7144 | 6.4 | 33 | -0.55 | 0.65 | 24 | 30.45 | 23.5425 | 573.2813
CR | S | 2.7144 | 6.84 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 408.4629
Canteen | W | 2.7144 | 39.2 | 33 | -0.55 | 0.65 | 24 | 30.45 | 23.5425 | 3511.3478
Canteen | E | 2.7144 | 44.8 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 3040.128
Canteen | S | 2.7144 | 50.8 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 3033.6134
Washing Area | E | 2.7144 | 10.27 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 696.9222
[9 empty] | Total Load: | 39227.8573
SECOND FLOOR
Space | Orientation | U | A(m^2) | CLTDsel | LM | k | Ti | Tave | CLTD adj | Q(W)
5 Bed Ward E | E | 2.7144 | 26 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 1400.3725
5 Bed Ward N | N | 2.7144 | 19.38 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 728.212
5 Bed Ward | N | 2.7144 | 19.38 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 728.212
Stairs N | N | 2.7144 | 43.2 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 1623.259
Stairs W | W | 2.7144 | 41.2 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 2800.5849
5-Bed Ward | N | 2.7144 | 19.38 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 728.212
5-Bed Ward N | N | 2.7144 | 19.38 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 728.212
5-Bed Ward W | W | 2.7144 | 26 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 1767.3594
Hallway (W) | W | 2.7144 | 9.7 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 659.361
Isolation room W | W | 2.7144 | 12.28 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 834.7374
Isolation room S | S | 2.7144 | 10.48 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 447.413
Isolation room CR | W | 2.7144 | 7.48 | 33 | -0.55 | 0.65 | 24 | 30.45 | 23.5425 | 478.0001
Private Room | W | 2.7144 | 9 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 611.7783
Private Room | W | 2.7144 | 9 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 611.7783
Private Room | W | 2.7144 | 9 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 611.7783
Private Room | W | 2.7144 | 9 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 611.7783
CSSR | W | 2.7144 | 13.05 | 33 | -0.55 | 0.65 | 24 | 30.45 | 23.5425 | 833.9441
Sterile Supply Room N | N | 2.7144 | 12 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 402.0461
Sterile Supply Room W | W | 2.7144 | 10.58 | 33 | -0.55 | 0.65 | 24 | 30.45 | 23.5425 | 676.1018
Recovery Room W | W | 2.7144 | 30.4 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 2066.451
Recovery Room S | S | 2.7144 | 21.6 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 922.149
Recovery Room CR | S | 2.7144 | 4.44 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 171.4749
Hallway (S) | S | 2.7144 | 19.2 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 819.688
Lounge Area | S | 2.7144 | 21.2 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 905.0722
DR-1 | S | 2.7144 | 5.04 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 215.1681
DR-2 | S | 2.7144 | 5.04 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 215.1681
DR-3 | S | 2.7144 | 5.04 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 215.1681
Anesthesia Off. And Storage | S | 2.7144 | 9.8 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 378.4807
Sterile Storage | S | 2.7144 | 8.8 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 339.8603
Clean-up Room | S | 2.7144 | 10.4 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 401.653
Sub-Ster Room | S | 2.7144 | 10.4 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 443.9977
Major Operating Room S | S | 2.7144 | 6 | 22 | -3.88 | 0.65 | 22 | 30.45 | 16.228 | 264.2957
Major Operating Room E | E | 2.7144 | 6 | 25 | -0.55 | 0.65 | 22 | 30.45 | 20.3425 | 331.3061
Fire Exit | E | 2.7144 | 8.6 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 463.2001
Delivery Room E | E | 2.7144 | 24 | 25 | -0.55 | 0.65 | 22 | 30.45 | 20.3425 | 1325.2244
Delivery Room N | N | 2.7144 | 9.4 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 353.2091
Chief of Clinics | E | 2.7144 | 12.9 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 694.8002
Conference Room | E | 2.7144 | 20.4 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 1098.7538
Chief of Hospital | E | 2.7144 | 8.16 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 439.5015
Reception (CR) | E | 2.7144 | 10.2 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 549.3769
Isolation Room S | S | 2.7144 | 12.28 | 22 | -0.55 | 0.65 | 22.5 | 30.45 | 17.8925 | 596.4077
Isolation Room E | E | 2.7144 | 8.88 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 478.2811
Isolation Room CR | E | 2.7144 | 7.84 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 422.2662
[9 empty] | Total Load: | 31394.0945
THIRD FLOOR
Space | Orientation | U | A(m^2) | CLTDsel | LM | k | Ti | Tave | CLTD adj | Q(W)
5 Bed Ward E | E | 2.7144 | 26 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 1764.36
5 Bed Ward N | N | 2.7144 | 19.4 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 684.5717
5 Bed Ward | N | 2.7144 | 19.4 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 684.5717
Stairs E | E | 2.7144 | 40.92 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 2776.8312
Stairs N | N | 2.7144 | 68 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 2399.5296
Stairs W | W | 2.7144 | 40.92 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 3665.4172
5 Bed Ward | N | 2.7144 | 19.4 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 684.5717
5 Bed Ward N | N | 2.7144 | 19.4 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 684.5717
5 Bed Ward W | W | 2.7144 | 26 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 2328.9552
Hallway | W | 2.7144 | 9.7 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 868.8794
Isolation Room W | W | 2.7144 | 13.4 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 1200.3077
Isolation Room CR | W | 2.7144 | 8.56 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 766.7637
Isolation Room S | S | 2.7144 | 12 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 716.6016
Private Room | W | 2.7144 | 10.6 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 949.4971
Private Room | W | 2.7144 | 10.6 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 949.4971
Private Room | W | 2.7144 | 10.6 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 949.4971
Private Room | W | 2.7144 | 10.6 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 949.4971
Solarium | W | 2.7144 | 11.65 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 1043.5511
Admitting N | N | 2.7144 | 12 | 13 | 2.22 | 0.65 | 22.5 | 30.45 | 13.843 | 423.4464
Admitting W | W | 2.7144 | 13.2 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 1182.3926
Billing | W | 2.7144 | 13.2 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 1182.3926
Cashier | W | 2.7144 | 10.4 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 931.5821
Personel's Dining W | W | 2.7144 | 7.69 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 688.8333
Personel's Dining CR W | W | 2.7144 | 7.16 | 33 | -0.55 | 0.65 | 22.5 | 30.45 | 25.0425 | 641.3584
Personel's Dining CR S | S | 2.7144 | 5.64 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 336.8028
Personel's Dining S | S | 2.7144 | 20.4 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 1218.2227
Stairs S | S | 2.7144 | 19.2 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 1146.5626
Female Toilet | S | 2.7144 | 11.28 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 673.6055
Male Toilet | S | 2.7144 | 11.28 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 673.6055
Hallway S | S | 2.7144 | 24 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 1433.2032
Water Tank S | S | 2.7144 | 48 | 22 | -3.88 | 0.65 | 24 | 30.45 | 14.228 | 2866.4064
Water Tank E | E | 2.7144 | 61.6 | 25 | -0.55 | 0.65 | 24 | 30.45 | 18.3425 | 4180.176
Water Tank N | N | 2.7144 | 8.88 | 13 | 2.22 | 0.65 | 24 | 30.45 | 12.343 | 313.3503
Solarium | E | 2.7144 | 11.67 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 791.9262
Private Room | E | 2.7144 | 10.6 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 719.316
Private Room | E | 2.7144 | 10.6 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 719.316
Private Room | E | 2.7144 | 10.6 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 719.316
Private Room | E | 2.7144 | 10.6 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 719.316
Isolation Room S | S | 2.7144 | 8.88 | 22 | -3.88 | 0.65 | 22.5 | 30.45 | 15.728 | 530.2852
Isolation Room E | E | 2.7144 | 13.4 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 909.324
Isolation Room CR | E | 2.7144 | 9.04 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 613.4544
Fire Exit | E | 2.7144 | 2.4 | 25 | -0.55 | 0.65 | 22.5 | 30.45 | 19.8425 | 162.864
[9 empty] | Total Load | 47844.5301

## GLASS LOAD
GLASS LOAD
FIRST FLOOR
Space | Orientation | U | To | Ti | A(m^2) | SHGF | SCL | SC | Qsg (W) | Qth (W)
Power House | E | 2.8722 | 34.5 | 22.5 | 2 | 685 | 0.8 | 0.55 | 602.8 | 68.9328
Maintenance Office | N | 2.8722 | 34.5 | 22.5 | 1.2 | 120 | 0.91 | 0.55 | 72.072 | 41.3597
Maintenance Office CR | N | 2.8722 | 34.5 | 22.5 | 0.36 | 120 | 0.91 | 0.55 | 21.6216 | 12.4079
Famale Toilet | N | 2.8722 | 34.5 | 24 | 0.72 | 120 | 0.91 | 0.55 | 43.2432 | 21.7138
Male Toilet | N | 2.8722 | 34.5 | 24 | 0.72 | 120 | 0.91 | 0.55 | 43.2432 | 21.7138
Minor Operating Room | N | 2.8211 | 34.5 | 22 | 1.6 | 120 | 0.91 | 0.55 | 96.096 | 56.422
Exaination/Treatment and Obs Area | N | 2.8722 | 34.5 | 22.5 | 2.2 | 120 | 0.91 | 0.55 | 132.132 | 75.8261
Exaination/Treatment and Obs Area CR | N | 2.8722 | 34.5 | 22.5 | 0.72 | 120 | 0.91 | 0.55 | 43.2432 | 24.8158
Emergency Room | W | 2.8722 | 34.5 | 22.5 | 2 | 685 | 0.82 | 0.55 | 617.87 | 68.9328
Hallway | W | 2.8722 | 34.5 | 22.5 | 2.75 | 685 | 0.82 | 0.55 | 849.5712 | 94.7826
Hallway | W | 2.8211 | 34.5 | 22.5 | 9 | 685 | 0.82 | 0.55 | 2780.415 | 304.6788
Ultrasound N | N | 2.8722 | 34.5 | 22.5 | 0.6 | 120 | 0.91 | 0.55 | 36.036 | 20.6798
Ultrasound W | W | 2.8722 | 34.5 | 22.5 | 4.2 | 685 | 0.82 | 0.55 | 1297.527 | 144.7589
Ultrasound CR | W | 2.8722 | 34.5 | 24 | 0.36 | 685 | 0.82 | 0.55 | 111.2166 | 10.8569
OPB Clinic OB-Gyne W | W | 2.8722 | 34.5 | 22.5 | 0.6 | 685 | 0.82 | 0.55 | 185.361 | 20.6798
OPB Clinic OB-Gyne S | S | 2.8722 | 34.5 | 22.5 | 1.6 | 230 | 0.83 | 0.55 | 167.992 | 55.1462
OPB Clinic OB-Gyne CR | S | 2.8722 | 34.5 | 24 | 0.36 | 230 | 0.83 | 0.55 | 37.7982 | 10.8569
Canteen W | W | 2.8722 | 34.5 | 24 | 4.2 | 685 | 0.82 | 0.55 | 1297.527 | 126.664
Canteen S | S | 2.8722 | 34.5 | 24 | 8.4 | 230 | 0.83 | 0.55 | 881.958 | 253.328
Canteen E | E | 2.8722 | 34.5 | 24 | 1.4 | 685 | 0.8 | 0.55 | 421.96 | 42.2213
Dietary | S | 2.8722 | 34.5 | 22.5 | 2.4 | 230 | 0.83 | 0.55 | 251.988 | 82.7194
Dietitian Office | S | 2.8722 | 34.5 | 22.5 | 2.8 | 230 | 0.83 | 0.55 | 293.986 | 96.5059
Cooking Area S | S | 2.8722 | 34.5 | 24 | 1.8 | 230 | 0.83 | 0.55 | 188.991 | 54.2846
Cooking Area E | E | 2.8722 | 34.5 | 24 | 2.4 | 685 | 0.8 | 0.55 | 723.36 | 72.3794
Washing Area | E | 2.8722 | 34.5 | 24 | 1.73 | 685 | 0.8 | 0.55 | 521.422 | 52.1735
Pressing Area | E | 2.8722 | 34.5 | 22.5 | 2 | 685 | 0.8 | 0.55 | 602.8 | 68.9328
Film File Storage | E | 2.8722 | 34.5 | 22.5 | 0.36 | 685 | 0.8 | 0.55 | 108.504 | 12.4079
Waiting Area CR | E | 2.8722 | 34.5 | 24 | 0.36 | 685 | 0.8 | 0.55 | 108.504 | 10.8569
Work Area Laboratory | E | 2.8722 | 34.5 | 22.5 | 2.4 | 685 | 0.8 | 0.55 | 723.36 | 82.7194
Cadaver Holding Room | E | 2.8722 | 34.5 | 22.5 | 1.6 | 685 | 0.8 | 0.55 | 482.24 | 55.1462
[7 empty] | Total: |  | 13744.8383 | 2064.9042
[7 empty] | Overall Total Load: |  | 15809.7425
SECOND FLOOR
Space | Orientation | U | To | Ti | A(m^2) | SHGF | SCL | SC | Qsg (W) | Qth (W)
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 4.62 | 120 | 0.91 | 0.55 | 277.4772 | 159.2348
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 4.62 | 120 | 0.91 | 0.55 | 277.4772 | 159.2348 | Awning or Sliding | 2.8722
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 4.62 | 120 | 0.91 | 0.55 | 277.4772 | 159.2348 | Fixed | 2.8211
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 4.62 | 120 | 0.91 | 0.55 | 277.4772 | 159.2348
Hallway | W | 2.8211 | 34.5 | 22.5 | 2.7 | 685 | 0.82 | 0.55 | 834.1245 | 91.4036
Isolation Room | W | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.82 | 0.55 | 432.509 | 48.253
Isolation Room CR | W | 2.8722 | 34.5 | 24 | 0.36 | 685 | 0.82 | 0.55 | 111.2166 | 10.8569
Private Room | W | 2.8722 | 34.5 | 22.5 | 3 | 685 | 0.82 | 0.55 | 926.805 | 103.3992
Private Room | W | 2.8722 | 34.5 | 22.5 | 3 | 685 | 0.82 | 0.55 | 926.805 | 103.3992
Private Room | W | 2.8722 | 34.5 | 22.5 | 3 | 685 | 0.82 | 0.55 | 926.805 | 103.3992
Private Room | W | 2.8722 | 34.5 | 22.5 | 3 | 685 | 0.82 | 0.55 | 926.805 | 103.3992
CSSR | W | 2.8722 | 34.5 | 22.5 | 1.95 | 685 | 0.82 | 0.55 | 602.4232 | 67.2095
Sterile Supply Room | W | 2.8722 | 34.5 | 24 | 5.02 | 685 | 0.82 | 0.55 | 1550.8537 | 151.3937
Recovery Room | S | 2.8722 | 34.5 | 22.5 | 2.4 | 230 | 0.83 | 0.55 | 251.988 | 82.7194
Recovery Room CR | S | 2.8722 | 34.5 | 24 | 0.36 | 230 | 0.83 | 0.55 | 37.7982 | 10.8569
Lounge Area | S | 2.8722 | 34.5 | 22.5 | 2.8 | 230 | 0.83 | 0.55 | 293.986 | 96.5059
DR 1 | S | 2.8722 | 34.5 | 22.5 | 0.36 | 230 | 0.83 | 0.55 | 37.7982 | 12.4079
DR 2 | S | 2.8722 | 34.5 | 22.5 | 0.36 | 230 | 0.83 | 0.55 | 37.7982 | 12.4079
DR 3 | S | 2.8722 | 34.5 | 22.5 | 0.36 | 230 | 0.83 | 0.55 | 37.7982 | 12.4079
Anesthesia Off. and Storage | S | 2.8722 | 34.5 | 24 | 1.6 | 230 | 0.83 | 0.55 | 167.992 | 48.253
Sterile Storage | S | 2.8722 | 34.5 | 24 | 1.6 | 230 | 0.83 | 0.55 | 167.992 | 48.253
Clean-up Room | S | 2.8722 | 34.5 | 24 | 1.6 | 230 | 0.83 | 0.55 | 167.992 | 48.253
Sub-Ster Room | S | 2.8722 | 34.5 | 22.5 | 1.6 | 230 | 0.83 | 0.55 | 167.992 | 55.1462
Chief of Clinics | E | 2.8722 | 34.5 | 22.5 | 2.1 | 685 | 0.8 | 0.55 | 632.94 | 72.3794
Conference Room | E | 2.8722 | 34.5 | 22.5 | 3.6 | 685 | 0.8 | 0.55 | 1085.04 | 124.079
Chief of Hospital | E | 2.8722 | 34.5 | 22.5 | 2.72 | 685 | 0.8 | 0.55 | 819.808 | 93.7486
Reception (CR) | S | 2.8722 | 34.5 | 22.5 | 1.2 | 230 | 0.83 | 0.55 | 125.994 | 41.3597
Isolation Room | E | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.8 | 0.55 | 421.96 | 48.253
Isolation Room CR | E | 2.8722 | 34.5 | 24 | 0.36 | 685 | 0.8 | 0.55 | 108.504 | 10.8569
[7 empty] | Total: |  | 12911.6367 | 2237.5402
[7 empty] | Overall Total Load |  | 15149.1769
THIRD FLOOR
Space | Orientation | U | To | Ti | A(m^2) | SHGF | SCL | SC | Qsg (W) | Qth (W)
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 2.31 | 120 | 0.91 | 0.55 | 138.7386 | 79.6174
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 2.31 | 120 | 0.91 | 0.55 | 138.7386 | 79.6174
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 2.31 | 120 | 0.91 | 0.55 | 138.7386 | 79.6174
5 Bed Ward | N | 2.8722 | 34.5 | 22.5 | 2.31 | 120 | 0.91 | 0.55 | 138.7386 | 79.6174
Hallway | W | 2.8722 | 34.5 | 22.5 | 2.7 | 685 | 0.82 | 0.55 | 834.1245 | 93.0593
Isolation Room | W | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.82 | 0.55 | 432.509 | 48.253
Private Room | W | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.82 | 0.55 | 432.509 | 48.253
Private Room | W | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.82 | 0.55 | 432.509 | 48.253
Private Room | W | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.82 | 0.55 | 432.509 | 48.253
Private Room | W | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.82 | 0.55 | 432.509 | 48.253
Solarium | W | 2.8211 | 34.5 | 22.5 | 3.35 | 685 | 0.82 | 0.55 | 1034.9322 | 113.4082
Admitting | W | 2.8722 | 34.5 | 22.5 | 2.4 | 685 | 0.82 | 0.55 | 741.444 | 82.7194
Billing | W | 2.8722 | 34.5 | 22.5 | 2.4 | 685 | 0.82 | 0.55 | 741.444 | 82.7194
Cashier | W | 2.8722 | 34.5 | 22.5 | 2.4 | 685 | 0.82 | 0.55 | 741.444 | 82.7194
Personel's Dining W | W | 2.8722 | 34.5 | 22.5 | 2.23 | 685 | 0.82 | 0.55 | 688.925 | 76.8601
Personel's Dining CR | W | 2.8722 | 34.5 | 24 | 0.36 | 685 | 0.82 | 0.55 | 111.2166 | 10.8569
Personel's Dining S | S | 2.8722 | 34.5 | 22.5 | 2.4 | 230 | 0.83 | 0.55 | 251.988 | 82.7194
Female Toilet | S | 2.8722 | 34.5 | 24 | 0.72 | 230 | 0.83 | 0.55 | 75.5964 | 21.7138
Male Toilet | S | 2.8722 | 34.5 | 24 | 0.72 | 230 | 0.83 | 0.55 | 75.5964 | 21.7138
Hallway S | S | 2.8722 | 34.5 | 22.5 | 0 | 230 | 0.83 | 0.55 | 0 | 0
Solarium | E | 2.8211 | 34.5 | 22.5 | 3.35 | 685 | 0.8 | 0.55 | 1009.69 | 113.4082
Private Room | E | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.8 | 0.55 | 421.96 | 48.253
Private Room | E | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.8 | 0.55 | 421.96 | 48.253
Private Room | E | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.8 | 0.55 | 421.96 | 48.253
Private Room | E | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.8 | 0.55 | 421.96 | 48.253
Isolation Room | E | 2.8722 | 34.5 | 22.5 | 1.4 | 685 | 0.8 | 0.55 | 421.96 | 48.253
Isolation Room CR | E | 2.8722 | 34.5 | 24 | 0.36 | 685 | 0.8 | 0.55 | 108.504 | 10.8569
[7 empty] | Total: |  | 11242.2046 | 1593.7539
[7 empty] | Overall Total Load |  | 12835.9585

## INFILTRATION LOAD
INFILTRATION LOAD
SPACE | Volume | L/s | To | Ti | Wo | Wi | Qs (W) | Ql (W)
1.1 Power House | 149.7544 | 10.982 | 34.5 | 22.5 | 0.018137 | 0.0092932 | 162.3577 | 291.3582
1.2 Work Area | 38.6048 | 2.831 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 41.8538 | 82.0102
1.3 Storage Room | 31.27 | 2.2019 | 34.5 | 24 | 0.018137 | 0.0092932 | 28.4842 | 58.4184
1.4 Maintenance Office | 65.238 | 4.7841 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 70.7284 | 138.5884
1.4 Maintenance Office CR | 11.35 | 0.79923 | 34.5 | 24 | 0.018137 | 0.0092932 | 10.3388 | 21.204
1.5 Female toilet | 73.1964 | 5.1542 | 34.5 | 24 | 0.018137 | 0.0092932 | 66.6753 | 136.745
1.6 Male Toilet | 73.3856 | 5.1676 | 34.5 | 24 | 0.018137 | 0.0092932 | 66.8477 | 137.0985
1.7 Minor Operating Room | 93.5544 | 6.9516 | 34.5 | 22 | 0.018137 | 0.0082198 | 107.0548 | 206.8172
1.8 Equipment and supply storage area | 22.44 | 1.5802 | 34.5 | 24 | 0.018137 | 0.0092932 | 20.4408 | 41.9223
1.9 Examination/Treatment Area | 168.77 | 12.3765 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 182.9737 | 358.5268
1.9 Examination/Treatment Area CR | 14.8348 | 1.0446 | 34.5 | 24 | 0.018137 | 0.0092932 | 13.5132 | 27.7143
1.10 Cadaver Holding Room | 78.5512 | 5.7604 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 85.1621 | 166.8703
1.11 Supply Room | 125.1572 | 9.1782 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 135.6904 | 265.8779
1.12 Bulk Storage | 15.9088 | 1.1202 | 34.5 | 24 | 0.018137 | 0.0092932 | 14.4915 | 29.7207
1.13 Pharmacy | 82.9948 | 6.0863 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 89.9796 | 176.3101
1.14 Medical Records Office | 71.8048 | 5.2657 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 77.8479 | 152.5386
1.15 Medical Records | 74.5232 | 5.465 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 80.7951 | 158.3135
1.16 PHILHEALTH | 68.5512 | 5.0271 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 74.3205 | 145.6268
1.17 Doctor's Duty | 46.4248 | 3.4045 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 50.3319 | 98.6226
1.18 Nurse Station (ER) | 523.8728 | 38.4173 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 567.9619 | 1112.8898
1.18 Nurse Station (ER) CR | 11.9092 | 0.83861 | 34.5 | 24 | 0.018137 | 0.0092932 | 10.8482 | 22.2487
HALLWAY | 2624.716 | 192.4792 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 2845.6121 | 5575.8187
1.21 Work Area (laboratory) | 131.44 | 9.7667 | 34.5 | 22 | 0.018137 | 0.0082198 | 150.4075 | 290.5695
1.23 Waiting area | 50.71 | 3.7187 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 54.9778 | 107.7259
1.23 Waiting area CR | 12.9452 | 0.91156 | 34.5 | 24 | 0.018137 | 0.0092932 | 11.7919 | 24.1841
1.24 OPD clinic dental 1 | 57.5244 | 4.2185 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.3657 | 122.202
1.25 OPD clinic dental 2 | 57.5244 | 4.2185 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.3657 | 122.202
1.26 Elevator | 35.8604 | 2.6298 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 38.8784 | 76.1801
1.27 OPD clinic surgery 1 | 57.7424 | 4.2344 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.602 | 122.6651
1.28 OPD clinic surgery 2 | 57.7424 | 4.2344 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.602 | 122.6651
1.29 Cashier | 21.95 | 1.6097 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 23.7973 | 46.6295
1.30 Billing | 22.04 | 1.6163 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 23.8949 | 46.8207
1.31 Admitting | 22.5452 | 1.6533 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 24.4426 | 47.8939
1.32 Film File Storage | 22.0812 | 1.5549 | 34.5 | 24 | 0.018137 | 0.0092932 | 20.114 | 41.2519
1.33 Radiologist Office | 36.5968 | 2.6838 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 39.6768 | 77.7445
1.34 Dark Room | 19.8088 | 1.4526 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 21.4759 | 42.0808
1.35 Control Booth | 101.0152 | 7.4078 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 109.5166 | 214.5918
1.37 OPD Clinic Pedia 1 | 57.5244 | 4.2185 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.3657 | 122.202
1.38 OPD Clinic Pedia 2 | 57.5244 | 4.2185 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.3657 | 122.202
1.39 OPD Records | 41.672 | 3.0559 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 45.1791 | 88.526
1.40 OPD info. And admitting | 39.922 | 2.9276 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 43.2818 | 84.8084
1.41 OPD Clinic Medical 1 | 57.7424 | 4.2344 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.602 | 122.6651
1.42 OPD Clinic Medical 2 | 57.7424 | 4.2344 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.602 | 122.6651
1.44 Waste Disposal Area | 57.4556 | 4.2134 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 62.2911 | 122.0559
1.46 Pressing Area | 33.724 | 2.4731 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.5622 | 71.6416
1.47 Linen Storage | 33.2548 | 2.3417 | 34.5 | 24 | 0.018137 | 0.0092932 | 30.2921 | 62.1264
1.49 Linen Office | 33.75 | 2.475 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 36.5904 | 71.6969
1.50 Admin Office | 54.428 | 3.9914 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 59.0087 | 115.6242
1.51 Male Toilet | 69.0396 | 4.8615 | 34.5 | 24 | 0.018137 | 0.0092932 | 62.8889 | 128.9793
1.53 Washing Area | 68.5068 | 5.0238 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 74.2723 | 145.5325
1.54 Receiving Sorting Area | 34.2844 | 2.5142 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 37.1698 | 72.8321
1.55 Administrative office | 141.2708 | 10.3599 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 153.1602 | 300.1088
1.56 Social Welfare | 54.3936 | 3.9889 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 58.9714 | 115.5511
1.57 Female Toilet | 68.1712 | 4.8004 | 34.5 | 24 | 0.018137 | 0.0092932 | 62.0978 | 127.357
1.58 OPD Info. And admitting | 41.7668 | 3.0629 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 45.2819 | 88.7274
1.59 OPD records | 46.3676 | 3.4003 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 50.2699 | 98.5011
1.60 Ultrasound | 76.3076 | 5.5959 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 82.7296 | 162.1041
1.60 Ultrasound CR | 10.1376 | 0.71386 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.2344 | 18.939
1.61 Cooking Area | 136.8608 | 9.6373 | 34.5 | 24 | 0.018137 | 0.0092932 | 124.6679 | 255.6824
1.62 Dry storage | 10.3764 | 0.73067 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.452 | 19.3851
1.63 Cold Storage | 7.85 | 0.55277 | 34.5 | 24 | 0.018137 | 0.0092932 | 7.1506 | 14.6653
1.64 Supply Receiving Area | 22.8736 | 1.6774 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 24.7986 | 48.5916
1.65 Dietician's Office | 36.9 | 2.706 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 40.0055 | 78.3886
1.65 Dietician's Office CR | 7.78 | 0.54784 | 34.5 | 24 | 0.018137 | 0.0092932 | 7.0869 | 14.5345
1.66 Dietary | 152.13 | 11.1562 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 164.9333 | 323.1776
1.67 Staff Dining | 203.5524 | 14.9272 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 220.6834 | 432.4168
1.68 OPD clinic Ob-gyne | 108.0224 | 7.9216 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 117.1136 | 229.4775
1.68 OPD clinic Ob-gyne CR | 10.1376 | 0.71386 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.2344 | 18.939
1.69 Garbage Disposal area | 9.12 | 0.6688 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 9.8875 | 19.3741
1.70 Canteen | 726.7968 | 51.1786 | 34.5 | 24 | 0.018137 | 0.0092932 | 662.0465 | 1357.7967
[5 empty] | Total |  | 8169.4957 | 16087.9229
[5 empty] | Total Load |  | 24257.4187
SECOND FLOOR
SPACE | Volume | L/s | To | Ti | Wo | Wi | Qs (W) | Ql (W)
5-Bed Ward 1 | 137.1076 | 10.0546 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 148.4053 | 291.2646
5-Bed Ward 1 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5217 | 19.56
5-Bed Ward 2 | 137.04 | 10.0496 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 148.3321 | 291.121
5-Bed Ward 2 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5217 | 19.56
Hallway 1 | 881.3296 | 64.6308 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 953.9512 | 1872.2532
Hallway 2 | 573.1645 | 42.0321 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 620.3933 | 1217.6025
Hallway 3 | 315.0296 | 23.1022 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 340.988 | 669.2334
Hallway 4 | 398.6188 | 29.232 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 431.465 | 846.8062
Hallway 5 | 571.5204 | 41.9115 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 618.6137 | 1214.1098
5-Bed Ward 3 | 137.16 | 10.0584 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 148.462 | 291.376
5-Bed Ward 3 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5217 | 19.56
5-Bed Ward 4 | 136.47 | 10.0078 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 147.7151 | 289.9102
5-Bed Ward 4 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5217 | 19.56
Isolation Room 1 | 54.6952 | 4.011 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 59.2021 | 116.1918
Isolation Room 1 CR | 10.4924 | 0.73884 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5421 | 19.6018
Private Room 1 | 55.6824 | 4.0834 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 60.2706 | 118.289
Private Room 1 CR | 10.462 | 0.7367 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5145 | 19.545
Private Room 2 | 55.5016 | 4.0701 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 60.0749 | 117.9049
Private Room 2 CR | 10.4788 | 0.73788 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5297 | 19.5764
Chief Nurse | 122.848 | 9.0089 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 132.9707 | 260.9722
Chief Nurse CR | 10.5496 | 0.74287 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5941 | 19.7087
Treatment Room | 71.7652 | 5.2628 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 77.6787 | 152.4545
Nurse Station | 91.316 | 6.6965 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 98.8404 | 193.9872
Nurse Station CR | 9.6484 | 0.67941 | 34.5 | 24 | 0.018137 | 0.0092932 | 8.7746 | 18.0251
Dirty Utility | 19.1476 | 1.3483 | 34.5 | 24 | 0.018137 | 0.0092932 | 17.4134 | 35.7714
Clean Linen | 9.8324 | 0.69236 | 34.5 | 24 | 0.018137 | 0.0092932 | 8.9419 | 18.3688
Private Room 3 | 55.494 | 4.0696 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 60.0667 | 117.8887
Private Room 3 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5217 | 19.56
Private Room 4 | 55.5712 | 4.0752 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 60.1503 | 118.0527
Private Room 4 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5217 | 19.56
Isolation Room 2 | 54.8264 | 4.0206 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 59.3441 | 116.4705
Isolation Room 2 CR | 10.4852 | 0.73833 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5356 | 19.5884
Reception | 44.2088 | 3.242 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 47.8516 | 93.915
Private Room 5 | 54.7252 | 4.0132 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 59.2346 | 116.2555
Private Room 5 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.6036 | 19.7281
Chief of Hospital | 74.9276 | 5.4947 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 81.1016 | 159.1725
Chief of Hospital CR | 27.7184 | 1.9518 | 34.5 | 24 | 0.018137 | 0.0092932 | 25.208 | 51.7833
3-Bed Ward 1 | 101.488 | 7.4425 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 109.8506 | 215.5961
3-Bed Ward 1 CR | 10.4348 | 0.73478 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.4897 | 19.4942
Elevator | 26.4604 | 1.9404 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 28.6407 | 56.2112
3-Bed Ward 2 | 101.92 | 7.4741 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 110.3182 | 216.5138
3-Bed Ward 2 CR | 10.4348 | 0.73478 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.4897 | 19.4942
Private Room 6 | 55.0048 | 4.0337 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 59.5372 | 116.8495
Private Room 6 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.6036 | 19.7281
Conference Room | 153.8148 | 11.2798 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 166.4891 | 326.7566
3-Bed Ward 3 | 101.488 | 7.4425 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 109.8506 | 215.5961
3-Bed Ward 3 CR | 10.4348 | 0.73478 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.4897 | 19.4942
3-Bed Ward 4 | 101.92 | 7.4741 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 110.3182 | 216.5138
3-Bed Ward 4 CR | 10.4348 | 0.73478 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.4897 | 19.4942
Private Room 7 | 55.0048 | 4.0337 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 59.5372 | 116.8495
Private Room 7 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.6036 | 19.7281
Private Room 8 | 55.0048 | 4.0337 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 59.5372 | 116.8495
Private Room 8 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.6036 | 19.7281
Chief of Clinics | 85.4464 | 6.2661 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 92.4872 | 181.5181
Chief of Clinics CR | 6.6584 | 0.46886 | 34.5 | 24 | 0.018137 | 0.0092932 | 6.0554 | 12.4392
CSSR | 125.7552 | 9.222 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 136.1174 | 267.1482
Delivery Room | 139.9448 | 10.3987 | 34.5 | 22 | 0.018137 | 0.0082198 | 159.8796 | 309.3707
Sub-Ster Room 1 | 21.6444 | 1.5241 | 34.5 | 24 | 0.018137 | 0.0092932 | 19.6841 | 40.4359
Labor Room | 102.9944 | 7.5529 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 111.4811 | 218.7962
Labor Room CR | 15.452 | 1.0881 | 34.5 | 24 | 0.018137 | 0.0092932 | 14.0525 | 28.8673
Pathologic Nursery | 67.1976 | 4.9278 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 72.7347 | 142.7513
Pre-mature nursery | 67.1996 | 4.928 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 72.7368 | 142.7555
Breastfeeding room | 40.9032 | 2.9996 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 44.2736 | 86.8927
Pre-operation area | 76.0028 | 5.6474 | 34.5 | 22 | 0.018137 | 0.0082198 | 86.8292 | 168.0165
Autoclave area | 59.95 | 4.3963 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 64.8899 | 127.3548
Autoclave area CR | 6.72 | 0.4732 | 34.5 | 24 | 0.018137 | 0.0092932 | 6.1114 | 12.5543
Sterile supply room | 86.4024 | 6.0842 | 34.5 | 24 | 0.018137 | 0.0092932 | 78.577 | 161.4164
Work Area 1 | 94.4012 | 6.9228 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 102.1799 | 200.5413
Major Operating Room | 140.17 | 10.4154 | 34.5 | 22 | 0.018137 | 0.0082198 | 160.1369 | 309.8685
Sub-Ster Room 2 | 22.7648 | 1.603 | 34.5 | 24 | 0.018137 | 0.0092932 | 20.703 | 42.5291
Jan.Clo. | 16.5352 | 1.1644 | 34.5 | 24 | 0.018137 | 0.0092932 | 15.0376 | 30.891
Clean up room | 51.64 | 3.6363 | 34.5 | 24 | 0.018137 | 0.0092932 | 46.963 | 96.4735
Sterile Instrument Supply Storage Area | 29.9136 | 2.1064 | 34.5 | 24 | 0.018137 | 0.0092932 | 27.2044 | 55.8844
Anesthesia Office & Storage | 70.0828 | 4.935 | 34.5 | 24 | 0.018137 | 0.0092932 | 63.7355 | 130.9282
DR-1 | 11.2 | 0.78867 | 34.5 | 24 | 0.018137 | 0.0092932 | 10.1856 | 20.9238
DR-2 | 11.2 | 0.78867 | 34.5 | 24 | 0.018137 | 0.0092932 | 10.1856 | 20.9238
DR-3 | 11.2 | 0.78867 | 34.5 | 24 | 0.018137 | 0.0092932 | 10.1856 | 20.9238
Lounge Area | 165.2084 | 12.1153 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 178.8216 | 350.9606
Recovery Room | 187.8968 | 13.7791 | 34.5 | 22.5 | 0.018137 | 0.0084806 | 203.3795 | 399.1587
Recovery Room CR | 8.3604 | 0.58871 | 34.5 | 24 | 0.018137 | 0.0092932 | 7.6032 | 15.6188
[5 empty] | Total: |  | 7292.9802 | 14355.1286
[5 empty] | Overall Total Load |  | 21648.1088
Space | Volume | L/s | To | Ti | Wo | Wi | Qs | Ql
5-Bed Ward 1 | 137.1076 | 10.0546 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 148.6466 | 291.2737
5-Bed Ward 1 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5372 | 19.56
5-Bed Ward 2 | 137.04 | 10.0496 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 148.5733 | 291.1301
5-Bed Ward 2 CR | 10.47 | 0.7678 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 11.3512 | 22.2426
Waiting Area 1 | 149.6348 | 10.9732 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 162.2281 | 317.8867
Waiting Area 2 | 149.6348 | 10.9732 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 162.2281 | 317.8867
5-Bed Ward 3 | 137.04 | 10.0496 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 148.5733 | 291.1301
5-Bed Ward 3 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5372 | 19.56
5-Bed Ward 4 | 137.04 | 10.0496 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 148.5733 | 291.1301
5-Bed Ward 4 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5372 | 19.56
Isolation Room 1 | 40.5572 | 2.9742 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 43.9705 | 86.1604
Isolation Room 1 CR | 10.4888 | 0.73859 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5544 | 19.5951
Private Room 1 | 55.6888 | 4.0838 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 60.3756 | 118.3062
Private Room 1 CR | 10.462 | 0.7367 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5299 | 19.545
Private Room 2 | 55.4952 | 4.0696 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 60.1657 | 117.895
Private Room 2 CR | 10.4744 | 0.73757 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5412 | 19.5682
Chief Nurse | 122.848 | 9.0089 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 133.1869 | 260.9804
Chief Nurse CR | 10.5496 | 0.74287 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.6097 | 19.7087
Treatment Room | 71.7652 | 5.2628 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 77.805 | 152.4592
Nurse Station | 91.316 | 6.6965 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 99.0012 | 193.9933
Nurse Station CR | 9.66 | 0.68022 | 34.5 | 24 | 0.018137 | 0.0092932 | 8.7994 | 18.0467
Dirty Utility | 19.1476 | 1.3483 | 34.5 | 24 | 0.018137 | 0.0092932 | 17.4417 | 35.7714
Clean Linen | 9.8324 | 0.69236 | 34.5 | 24 | 0.018137 | 0.0092932 | 8.9564 | 18.3688
Private Room 3 | 55.494 | 4.0696 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 60.1644 | 117.8924
Private Room 3 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5372 | 19.56
Private Room 4 | 55.5712 | 4.0752 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 60.2481 | 118.0564
Private Room 4 CR | 10.47 | 0.73726 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5372 | 19.56
Isolation Room 2 | 40.6864 | 2.9837 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 44.1106 | 86.4349
Isolation Room 2 CR | 10.4852 | 0.73833 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.5511 | 19.5884
Private Room 5 | 63.4476 | 4.6528 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 68.7874 | 134.7892
Private Room 5 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.6192 | 19.7281
Private Room 6 | 63.4476 | 4.6528 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 68.7874 | 134.7892
Private Room 6 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.6192 | 19.7281
3-Bed Ward 1 | 99.132 | 7.2697 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 107.4749 | 210.5977
3-Bed Ward 1 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.6192 | 19.7281
3-Bed Ward 2 | 99.5636 | 7.3013 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 107.9429 | 211.5146
3-Bed Ward 2 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.6192 | 19.7281
Private Room 7 | 54.7252 | 4.0132 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 59.3309 | 116.2592
Private Room 7 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.6192 | 19.7281
Private Room 8 | 55.0048 | 4.0337 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 59.634 | 116.8531
Private Room 8 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.6192 | 19.7281
Private Room 9 | 64.0448 | 4.6966 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 69.4348 | 136.0579
Private Room 9 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.6192 | 19.7281
Private Room 10 | 64.0448 | 4.6966 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 69.4348 | 136.0579
Private Room 10 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.6192 | 19.7281
Elevator | 35.8604 | 2.6298 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 38.8784 | 76.1825
Private Room 11 | 55.0048 | 4.0337 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 59.634 | 116.8531
Private Room 11 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.6192 | 19.7281
Private Room 12 | 55.0048 | 4.0337 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 59.634 | 116.8531
Private Room 12 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.6192 | 19.7281
Waiting Area | 93.9316 | 6.8883 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 101.8369 | 199.5499
Private Room 13 | 43.0288 | 3.1554 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 46.6501 | 91.4111
Private Room 13 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.6192 | 19.7281
Private Room 14 | 45.26 | 3.3191 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 49.0691 | 96.1511
Private Room 14 CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.6192 | 19.7281
Solarium 1 | 53.2332 | 3.9038 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 57.7133 | 113.0895
Stretcher's Wheelchair Nook 1 | 44.3488 | 3.2522 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 48.0812 | 94.2154
Stretcher's Wheelchair Nook 2 | 33.1 | 2.4273 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 35.8857 | 70.3182
Solarium 2 | 53.87 | 3.9505 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 58.4037 | 114.4424
Water Tank 1 and 2 | 735.7752 | 53.9568 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 797.698 | 1563.0935
Chapel | 235.4404 | 17.2656 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 255.2551 | 500.1736
Male Toilet | 69.7808 | 4.9137 | 34.5 | 24 | 0.018137 | 0.0092932 | 63.564 | 130.364
Female Toilet | 69.9224 | 4.9237 | 34.5 | 24 | 0.018137 | 0.0092932 | 63.693 | 130.6285
Waiting Area | 174.3656 | 12.7868 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 189.0402 | 370.4253
Admitting | 43.6024 | 3.1975 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 47.272 | 92.6297
Billing | 43.1324 | 3.163 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 46.7624 | 91.6312
Cashier | 37.6652 | 2.7621 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 40.8351 | 80.0166
Personel's dining | 107.9832 | 7.9188 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 117.0711 | 229.4014
Personel's dining CR | 10.56 | 0.7436 | 34.5 | 24 | 0.018137 | 0.0092932 | 9.6192 | 19.7281
HALLWAY | 2512.0732 | 184.2187 | 34.5 | 22.5 | 0.018137 | 0.0084803 | 2723.4893 | 5336.6916
[5 empty] | Total |  | 7336.2148 | 14410.357
[5 empty] | Total Load |  | 21746.5718

## MISCELLANEOUS LOAD
GROUND FLOOR
SPACE | Equipment | WATTAGE | Cs | Cl | CLF | Qs (W) | Ql (W)
Maintenance office | CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 70.8 | 0.33 | 0.16 | 0.96 | 22.4294 | 11.328
Minor operating room | SMOKE DETECTOR, 0.4W CARDIOPULMONARY BYPASS MACHINE, 150 W SURGICAL LGHTS, 25W AUTOCLAVE, 2000W ELECTROSURGERY, 109 W | 2284.4 | 0.33 | 0.16 | 0.96 | 723.6979 | 365.504
Examination/Treament Area | CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 70.8 | 0.33 | 0.16 | 0.96 | 22.4294 | 11.328
Supply Room | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Pharmacy | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Medical records office | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Philhealth | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Doctors on duty | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Emergency room | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Patho. office | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Radiologist office | TV, 125W TELEPHONE, 5W SMOKE DETECTOR, 1.6W CEILING ORBITAL FAN, 70W | 201.6 | 0.33 | 0.16 | 0.96 | 63.8669 | 32.256
X-ray Room | X-RAY MACHINE, 1500W SMOKE DETECTOR, 0.8W | 1500.8 | 0.33 | 0.16 | 0.96 | 475.4534 | 240.128
OPD Clinic Dental 1 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic Dental 2 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic surgery 1 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic surgery 1 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic Pedia 1 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic Pedia 2 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic Medical 1 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD Clinic Medical 2 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD info and admitting 1 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
OPD ob-gyne | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Cashier | TV, 125W TELEPHONE, 5W CASH REGISTER, 100W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 525.8 | 0.33 | 0.16 | 0.96 | 166.5734 | 84.128
Billing | TV, 125W TELEPHONE, 5W CASH REGISTER, 100W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 525.8 | 0.33 | 0.16 | 0.96 | 166.5734 | 84.128
Admitting | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Administrative Office | TELEPHONE, 5W TV, 125W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 425.8 | 0.33 | 0.16 | 0.96 | 134.8934 | 68.128
Admin Office | TELEPHONE, 5W TV, 125W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 425.8 | 0.33 | 0.16 | 0.96 | 134.8934 | 68.128
Social Welfare | TELEPHONE, 5W TV, 125W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 425.8 | 0.33 | 0.16 | 0.96 | 134.8934 | 68.128
OPD info and admitting 2 | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Ultrasound | TV, 150W TELEPHONE, 5W ULTRASOUND MACHINE, 95W SMOKE DETECTOR, 0.4W | 250.4 | 0.33 | 0.16 | 0.96 | 79.3267 | 40.064
OPD ob-gyne | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Canteen | TV, 150W TELEPHONE, 5W SMOKE DETECTOR, 1.2W CEILING ORBITAL FAN, 70W EXHAUST FAN, 40W | 266.2 | 0.33 | 0.16 | 0.96 | 84.3322 | 42.592
Dietitians office | TV, 150W TELEPHONE, 5W SMOKE DETECTOR, 0.4W | 155.4 | 0.33 | 0.16 | 0.96 | 49.2307 | 24.864
dry storage | SMOKE DETECTOR, 0.4W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
cold storage | SMOKE DETECTOR, 0.4W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Supply recieving area | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Cadaver Holding Room | SMOKE DETECTOR, 0.4W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Nurse Station | TV, 125 W TELEPHONE, 5 W COMPUTER, 225 W | 355 | 0.33 | 0.16 | 0.96 | 112.464 | 56.8
Hallway | SMOKE DETECTOR, 0.8W SPEAKER, 4W FIRE ALARM, 1 W CCTV(14), 56W | 61.8 | 0.33 | 0.16 | 0.96 | 19.5782 | 9.888
Cooking Area | OVEN, 1200 W REFRIGERATOR, 780W WATER DISPENSER, 600W | 2580 | 0.33 | 0.16 | 0.96 | 817.344 | 412.8
Staff Dining | SMOKE DETECTOR, 0.4W FRIDGE, 150W WATER DISPENSER, 600W | 750.4 | 0.33 | 0.16 | 0.96 | 237.7267 | 120.064
|  |  |  | Total |  | 5447.2493 | 2751.136
|  |  |  | Total Load |  | 8198.3853
SECOND FLOOR PLAN
SPACE | Equipment | Wattage | CS | Cl | CLF | Qs (W) | Ql (W)
5- Bed Ward 1 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
5- Bed Ward 2 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
5- Bed Ward 3 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
5- Bed Ward 4 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
Isolation Room | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W WALL FAN,25 W | 5.4 | 0.33 | 0.16 | 0.96 | 1.7107 | 0.864
Private Room 1 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 2 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 3 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 4 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 5 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 6 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 7 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 8 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Isolation Room 2 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W | 5.4 | 0.33 | 0.16 | 0.96 | 1.7107 | 0.864
Chief Nurse | SMOKE DETECTOR, 0.4W TELEPHONE, 5W COMPUTER, 225W | 230.4 | 0.33 | 0.16 | 0.96 | 72.9907 | 36.864
Treatment Room | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 70.4 | 0.33 | 0.16 | 0.96 | 22.3027 | 11.264
Nurse Station | TV, 125 W TELEPHONE, 5 W COMPUTER, 225 W | 355 | 0.33 | 0.16 | 0.96 | 112.464 | 56.8
Reception | SMOKE DETECTOR, 0.4W TELEPHONE, 5W | 5.4 | 0.33 | 0.16 | 0.96 | 1.7107 | 0.864
Chief of Hospital | TELEPHONE, 5W TV, 125W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 425.8 | 0.33 | 0.16 | 0.96 | 134.8934 | 68.128
Conference Room | TELEPHONE, 5W TV, 125W COMPUTER, 225W WATER DISPENSER, 600 W SMOKE DETECTOR, 0.8 W | 955.8 | 0.33 | 0.16 | 0.96 | 302.7974 | 152.928
Chief of Clinics | TELEPHONE, 5W TV, 125W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 425.8 | 0.33 | 0.16 | 0.96 | 134.8934 | 68.128
3-Bed Ward 1 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
3-Bed Ward 2 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
3-Bed Ward 3 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
3-Bed Ward 4 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
Delivery Room | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Labor Room | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Pathologic Nursery | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Pre-Mature Nursery | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
BreastFeeding Room | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Pre-operation Area | SMOKE DETECTOR, 0.4W CARDIOPULMONARY BYPASS MACHINE, 150 W SURGICAL LGHTS, 25W AUTOCLAVE, 2000W | 2175.4 | 0.33 | 0.16 | 0.96 | 689.1667 | 348.064
Autoclave Area | AUTOCLAVE, 1400 W SMOKE DETECTOR, 0.4 W | 1400.4 | 0.33 | 0.16 | 0.96 | 443.6467 | 224.064
Sterile Supply Room | TELEPHONE, 15W SMOKE DETECTOR, 0.4 W FRIDGE, 200 W | 215.4 | 0.33 | 0.16 | 0.96 | 68.2387 | 34.464
Recovery Room | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Lounge Area | SMOKE DETECTOR, 0.4 W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Anesthesia Office | SMOKE DETECTOR 0.4 W TELEPHONE, 5 W COMPUTER, 225 W ANESTHESIA SYSTEM, 166 W | 396.4 | 0.33 | 0.16 | 0.96 | 125.5795 | 63.424
Nurse Station | TV, 125 W TELEPHONE, 5 W COMPUTER, 225 W | 355 | 0.33 | 0.16 | 0.96 | 112.464 | 56.8
Major Operating Room | SMOKE DETECTOR, 0.4 W CARDIOPULMONARY BYPASS MACHINE, 150 W SURGICAL LGHTS, 25W VACUUM SUCTION, 302 W AUTOCLAVE, 2000W | 2477.4 | 0.33 | 0.16 | 0.96 | 784.8403 | 396.384
Clean Up Room | SMOKE DETECTOR, 0.4W | 0.4 | 0.33 | 0.16 | 0.96 | 0.12672 | 0.064
Hallway | SMOKE DETECTOR, 0.8W SPEAKER, 4W FIRE ALARM 1 W CCTV (10), 40 W | 45.8 | 0.33 | 0.16 | 0.96 | 14.5094 | 7.328
|  |  |  | Total |  | 3484.8253 | 1760.0128
|  |  |  | Total Load |  | 5244.8381
THIRD FLOOR PLAN
SPACE | Equipment | Wattage | Cs | Cl | CLF | Qs (W) | Qw (W)
5- Bed Ward 1 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
5- Bed Ward 2 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
5- Bed Ward 3 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
5- Bed Ward 4 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
Isolation Room | SMOKE DETECTOR, 0.4W TELEPHONE, 5W WALL FAN, 25W TV, 150 W | 175.9 | 0.33 | 0.16 | 0.96 | 55.7251 | 28.144
Private Room 1 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 2 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 3 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 4 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 5 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 6 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 7 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 8 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 9 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 10 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 11 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 12 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 13 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 14 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 15 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Private Room 16 | SMOKE DETECTOR, 0.4W TELEPHONE, 5W TV, 150 W MINIFRIDGE,0.66W | 156.06 | 0.33 | 0.16 | 0.96 | 49.4398 | 24.9696
Chief Nurse | SMOKE DETECTOR, 0.4W TELEPHONE, 5W COMPUTER, 225W | 230.4 | 0.33 | 0.16 | 0.96 | 72.9907 | 36.864
Treatment Room | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 70W | 70.4 | 0.33 | 0.16 | 0.96 | 22.3027 | 11.264
Nurse Station | TV, 125 W TELEPHONE, 5 W COMPUTER, 225 W | 355 | 0.33 | 0.16 | 0.96 | 112.464 | 56.8
3-Bed Ward 1 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
3-Bed Ward 2 | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
Admitting | TELEPHONE, 5W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 300.8 | 0.33 | 0.16 | 0.96 | 95.2934 | 48.128
Billing | TV, 125W TELEPHONE, 5W CASH REGISTER, 100W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 525.8 | 0.33 | 0.16 | 0.96 | 166.5734 | 84.128
Cashier | TV, 125W TELEPHONE, 5W CASH REGISTER, 100W COMPUTER, 225W CEILING ORBITAL FAN, 70W SMOKE DETECTOR, 0.8W | 525.8 | 0.33 | 0.16 | 0.96 | 166.5734 | 84.128
Personel's Dining | SMOKE DETECTOR, 0.4W Fridge, 150W WATER, DISPENSER 600W Oven 1200W | 1950.4 | 0.33 | 0.16 | 0.96 | 617.8867 | 312.064
Chapel | HEAT DETECTOR, 0.16 W CEILING ORBITAL FAN, 50 W | 50.16 | 0.33 | 0.16 | 0.96 | 15.8907 | 8.0256
Solarium | SMOKE DETECTOR, 0.4W CEILING ORBITAL FAN, 25W | 25.4 | 0.33 | 0.16 | 0.96 | 8.0467 | 4.064
Hallway | SMOKE DETECTOR, 0.8W SPEAKER, 4W FIRE ALARM,1W CCTV (10), 40W | 45.8 | 0.33 | 0.16 | 0.96 | 14.5094 | 7.328
|  |  |  | Total |  | 2187.5737 | 1104.8352
|  |  |  | Total Load |  | 3292.4089

## ROOF LOAD
THIRD FLOOR
TYPE 6, roof without suspended ceiling
SPACE | U | Area (m2) | CLTDmax | Ti | Tave | CLTDadj | Q(W)
5-Bed Ward 1 | 2.5844 | 34.2769 | 18 | 22.5 | 30.45 | 13.0875 | 1159.3501
5-Bed Ward 2 | 2.5844 | 34.26 | 18 | 22.5 | 30.45 | 13.0875 | 1158.7785
Waiting Area 1 | 2.5844 | 37.4087 | 18 | 22.5 | 30.45 | 13.0875 | 1265.2772
Waiting Area 2 | 2.5844 | 37.4087 | 18 | 22.5 | 30.45 | 13.0875 | 1265.2772
5-Bed Ward 3 | 2.5844 | 34.26 | 18 | 22.5 | 30.45 | 13.0875 | 1158.7785
5-Bed Ward 4 | 2.5844 | 34.26 | 18 | 22.5 | 30.45 | 13.0875 | 1158.7785
Isolation Room 1 | 2.5844 | 10.1393 | 18 | 22.5 | 30.45 | 13.0875 | 342.9423
Private Room 1 | 2.5844 | 13.9222 | 18 | 22.5 | 30.45 | 13.0875 | 470.8916
Private Room 2 | 2.5844 | 13.8738 | 18 | 22.5 | 30.45 | 13.0875 | 469.2546
Chief Nurse | 2.5844 | 30.712 | 18 | 22.5 | 30.45 | 13.0875 | 1038.7742
Treatment Room | 2.5844 | 17.9413 | 18 | 22.5 | 30.45 | 13.0875 | 606.8299
Nurse Station | 2.5844 | 22.829 | 18 | 22.5 | 30.45 | 13.0875 | 772.1469
Dirty Utility | 2.5844 | 4.7869 | 18 | 24 | 30.45 | 11.9625 | 147.9901
Clean Linen | 2.5844 | 2.4581 | 18 | 24 | 30.45 | 11.9625 | 75.9937
Private Room 3 | 2.5844 | 13.8735 | 18 | 22.5 | 30.45 | 13.0875 | 469.2444
Private Room 4 | 2.5844 | 13.8928 | 18 | 22.5 | 30.45 | 13.0875 | 469.8972
Isolation Room 2 | 2.5844 | 10.1716 | 18 | 22.5 | 30.45 | 13.0875 | 344.0348
Private Room 5 | 2.5844 | 15.8619 | 18 | 22.5 | 30.45 | 13.0875 | 536.4982
Private Room 6 | 2.5844 | 15.8619 | 18 | 22.5 | 30.45 | 13.0875 | 536.4982
3-Bed Ward 1 | 2.5844 | 24.783 | 18 | 22.5 | 30.45 | 13.0875 | 838.2372
3-Bed Ward 2 | 2.5844 | 24.8909 | 18 | 22.5 | 30.45 | 13.0875 | 841.8867
Private Room 7 | 2.5844 | 13.6813 | 18 | 22.5 | 30.45 | 13.0875 | 462.7436
Private Room 8 | 2.5844 | 13.7512 | 18 | 22.5 | 30.45 | 13.0875 | 465.1078
Private Room 9 | 2.5844 | 16.0112 | 18 | 22.5 | 30.45 | 13.0875 | 541.548
Private Room 10 | 2.5844 | 16.0112 | 18 | 22.5 | 30.45 | 13.0875 | 541.548
Elevator | 2.5844 | 8.9651 | 18 | 22.5 | 30.45 | 13.0875 | 303.2272
Private Room 11 | 2.5844 | 13.7512 | 18 | 22.5 | 30.45 | 13.0875 | 465.1078
Private Room 12 | 2.5844 | 13.7512 | 18 | 22.5 | 30.45 | 13.0875 | 465.1078
Waiting Area | 2.5844 | 23.4829 | 18 | 22.5 | 30.45 | 13.0875 | 794.2638
Private Room 13 | 2.5844 | 10.7572 | 18 | 22.5 | 30.45 | 13.0875 | 363.8416
Private Room 14 | 2.5844 | 11.315 | 18 | 22.5 | 30.45 | 13.0875 | 382.7081
Solarium 1 | 2.5844 | 13.3083 | 18 | 22.5 | 30.45 | 13.0875 | 450.1276
Stretcher's Wheelchair Nook 1 | 2.5844 | 11.0872 | 18 | 22.5 | 30.45 | 13.0875 | 375.0032
Stretcher's Wheelchair Nook 2 | 2.5844 | 8.275 | 18 | 22.5 | 30.45 | 13.0875 | 279.8859
Solarium 2 | 2.5844 | 13.4675 | 18 | 22.5 | 30.45 | 13.0875 | 455.5122
Water Tank 1 and 2 | 2.5844 | 183.9438 | 18 | 22.5 | 30.45 | 13.0875 | 6221.5446
Chapel | 2.5844 | 58.8601 | 18 | 22.5 | 30.45 | 13.0875 | 1990.8295
Waiting Area | 2.5844 | 43.5914 | 18 | 22.5 | 30.45 | 13.0875 | 1474.3951
Admitting | 2.5844 | 10.9006 | 18 | 22.5 | 30.45 | 13.0875 | 368.6918
Billing | 2.5844 | 10.7831 | 18 | 22.5 | 30.45 | 13.0875 | 364.7176
Cashier | 2.5844 | 9.4163 | 18 | 22.5 | 30.45 | 13.0875 | 318.4882
Personel's dining | 2.5844 | 26.9958 | 18 | 22.5 | 30.45 | 13.0875 | 913.0809
[6 empty] | Total Load | 33124.8407

## PARTITION LOAD
Space | Spaces | U | A | Ti | Ti2 | Q | Window | Door | Wall
Power House | Hallway |  | 22.2 |  |  |  |  | 1.8 | 24
| Work Area |  | 14.52 |  |  |  |  | 0 | 14.52
| Storage Room |  | 11.6 |  |  |  |  | 0 | 11.6
Work Area | Storage Room |  | 10.2 |  |  |  |  | 1.8 | 12
| Maintenance Room |  | 12.72 |  |  |  |  | 1.8 | 14.52
Storage Room | Hallway |  | 12 |  |  |  |  | 0 | 12
| Maintenance Room |  | 11.6 |  |  |  |  | 0 | 11.6
Maintenance Room | Hallway |  | 28 |  |  |  |  | 1.8 | 29.8
| Maintenance Room CR |  | 11.68 |  |  |  |  | 1.8 | 13.48
Female Toilet | Hallway |  | 36.2 |  |  |  |  | 1.8 | 38
Male Toilet | Hallway |  | 36.2 |  |  |  |  | 1.8 | 38
Minor Operating Room | Hallway |  | 24.2 |  |  |  |  | 1.8 | 26
| Emergency Room |  | 18.8 |  |  |  |  | 3.6 | 22.4
| Examination/Treatment OBS CR |  | 7.72 |  |  |  |  | 0 | 7.72
| Equipment and Supply Storage Area |  | 11.2 |  |  |  |  | 0 | 11.2
Equipment and Supply Storage | Emergency Room |  | 7 |  |  |  |  | 1.8 | 8.8
| Examination/Treatment OBS CR |  | 8.8 |  |  |  |  | 0 | 8.8
Examination/Treatment OBS | Examination/Treatment OBS CR |  | 5.92 |  |  |  |  | 1.8 | 7.72
Emergency Room | Hallway |  | 36.2 | [5 empty] | 36.2
| Doctor's on Duty CR |  | 3.4 |  |  |  |  | 1.8 | 5.2
| Doctor's on Duty |  | 23.76 |  |  |  |  | 1.8 | 25.56
Doctor's on Duty | Doctor's on Duty CR |  | 10.4 |  |  |  | 0 | 0 | 10.4
| Hallway |  | 10.6 |  |  |  | 1.4 | 0 | 12
Cadaver Holding Room | Hallway |  | 10.4 |  |  |  | 0 | 3.6 | 14
| Supply Room |  | 0
| Work Area Laboratory |  | 5.2 |  |  |  | 0 | 0 | 5.2
Supply Room | Hallway |  | 0
| Pathology Office Laboratory |  | 22 |  |  |  | 0 | 0 | 22
Pharmacy | Bulk Storage |  | 15.4 |  |  |  |  | 1.8 | 17.2
| Hallway |  | 54.2 |  |  |  | 2.8 | 1.8 | 58.8
| Medical Record Office |  | 24 |  |  |  | 0 | 0 | 24
Bulk Storage | Hallway |  | 16.8 |  |  |  | 0 | 0 | 16.8
Medical Record Office | Hallway |  | 45.32 |  |  |  | 4.08 | 1.8 | 51.2
| Philhealth |  | 24 |  |  |  | 0 | 0 | 24
Philhealth | Hallway |  | 43.8 |  |  |  | 2.4 | 1.8 | 48
Work Area Laboratory | Waiting Area CR |  | 9 |  |  |  | 0 | 0 | 9
| Waiting Area |  | 19.8 |  |  |  | 0 | 1.8 | 21.6
| Hallway |  | 12.2 |  |  |  | 0 | 0 | 12.2
Film File Storage | Wating Area CR |  | 8.8 |  |  |  | 0 | 0 | 8.8
| Waiting Area |  | 5.8 |  |  |  | 0 | 0 | 5.8
| Dark Room |  | 14.6 |  |  |  | 0 | 0 | 14.6
| Radiologist Office |  | 4.84 |  |  |  | 0 | 1.8 | 6.64
Waiting Area | Waiting Area CR |  | 4.6 |  |  |  | 0 | 1.8 | 6.4
| Hallway |  | 16 |  |  |  | 0 | 2.4 | 18.4
Dark Room | Radiologist Office |  | 6 |  |  |  | 0 | 0 | 6
| Waste Disposal Area |  | 6 |  |  |  | 0 | 0 | 6
| X-Ray Room CR |  | 6.8 |  |  |  | 0 | 0 | 6.8
| X Ray Room |  | 13 |  |  |  | 0 | 1.6 | 14.6
Radiogist Office | Hallway |  | 9.4 |  |  |  | 1.4 | 1.8 | 12.6
| X Ray Room |  | 10.6 |  |  |  | 0 | 1.8 | 12.4
X Ray Room | Waste Disposal Area |  | 14.32 |  |  |  | 0 | 0 | 14.32
| Linen Storage |  | 19.4 |  |  |  | 0 | 0 | 19.4
| Pressing Area |  | 3.4 |  |  |  | 0 | 0 | 3.4
| Hallway |  | 21.72 |  |  |  | 0 | 2.4 | 24.12
Pressing Area | Washing Area |  | 10.2 |  |  |  | 0 | 1.8 | 12
| Linen Storage |  | 10.2 |  |  |  | 0 | 1.8 | 12
| Waste Disposal Area |  | 8.88 |  |  |  | 0 | 0 | 8.88
Linen Storage | Washing Area |  | 22 |  |  |  | 0 | 1.8 | 23.8
| Hallway |  | 10.72 |  |  |  | 1.4 | 0 | 12.12
Washing Area | Washing Area CR |  | 17.2 |  |  |  | 0 | 1.6 | 18.8
| Hallway |  | 38 |  |  |  | 0 | 2 | 40
OPD Clinic Dental | Hallway |  | 28.4 |  |  |  | 1.2 | 2.4 | 32
| OPD Clinic Dental |  | 19.44 |  |  |  | 0 | 0 | 19.44
| OPD Clinic Pedia |  | 12.56 |  |  |  | 0 | 0 | 12.56
OPD Clinic Dental | Hallway |  | 18.4 |  |  |  | 1.2 | 2.4 | 22
| OPD Clinic Pedia |  | 12.56 |  |  |  | 0 | 0 | 12.56
| Elevator |  | 10 |  |  |  | 0 | 0 | 10
OPD Clinic Pedia | Hallway |  | 28.4 |  |  |  | 1.2 | 2.4 | 32
| OPD Clinic Pedia |  | 19.44 |  |  |  | 0 | 0 | 19.44
OPD Clinic Pedia | Hallway |  | 8.96 |  |  |  | 1.2 | 2.4 | 12.56
| OPD Records |  | 9.92 |  |  |  | 0 | 0 | 9.92
| OPD Info & Admitting |  | 9.52 |  |  |  | 0 | 0 | 9.52
OPD Records | Elevator |  | 19.2 |  |  |  | 0 | 0 | 19.2
| OPD Info & Admitting |  | 17.6 |  |  |  | 0 | 1.6 | 19.2
Elevator | Hallway |  | 19.2 |  |  |  | 0 | 0 | 19.2
| OPD Clinic Surgery |  | 10 |  |  |  | 0 | 0 | 10
OPD Info & Admitting | Hallway |  | 16.4 |  |  |  | 1.2 | 1.6 | 19.2
| OPD Clinic Medical |  | 9.52 |  |  |  | 0 | 0 | 9.52
OPD Clinic Surgery | Hallway |  | 18.64 |  |  |  | 1.2 | 1.6 | 21.44
| OPD Clinic Surgery |  | 19.2 |  |  |  | 0 | 0 | 19.2
| OPD Clinic Medical |  | 12 |  |  |  | 0 | 0 | 12
OPD Clinic Medical | OPD Clinic Medical |  | 19.2 |  |  |  | 0 | 0 | 19.2
| Hallway |  | 9.2 |  |  |  | 1.2 | 1.6 | 12
OPD Clinic Surgery | Hallway |  | 28.64 |  |  |  | 1.2 | 1.6 | 31.44
| OPD Clinic Medical |  | 12 |  |  |  | 0 | 0 | 12
OPD Clinic Medical | Hallway |  | 28.64 |  |  |  | 1.2 | 1.6 | 31.44
Cashier | Billing |  | 12 |  |  |  | 0 | 0 | 12
| Hallway |  | 25.8 |  |  |  |  | 1.8 | 27.6
Billing | Hallway |  | 13.8 |  |  |  |  | 1.8 | 15.6
| Admitting |  | 12 |  |  |  |  | 0 | 12
Admitting | Hallway |  | 13.8 |  |  |  |  | 1.8 | 15.6
Administrative Office | Admin Office |  | 10.4 |  |  |  | 0 | 1.8 | 12.2
| Social Welfare |  | 12.2 |  |  |  | 0 | 0 | 12.2
| Hallway |  | 63 |  |  |  | 7.2 | 1.8 | 72
Admin Office | Social Welfare |  | 19.2 |  |  |  | 0 | 0 | 19.2
| Hallway |  | 16.8 |  |  |  | 2.4 | 0 | 19.2
| Male Toilet |  | 12 |  |  |  | 0 | 0 | 12
Social Welfare | Hallway |  | 15 |  |  |  | 2.4 | 1.8 | 19.2
| Female Toilet |  | 12 |  |  |  | 0 | 0 | 12
Male Toilet | Hallway |  | 33 |  |  |  | 1.2 | 1.8 | 36
| Female Toilet |  | 24 |  |  |  | 0 | 0 | 24
Female Toilet | Hallway |  | 33 |  |  |  | 1.2 | 1.8 | 36
OPD Info & Admitting | Hallway |  | 23.84 |  |  |  | 1.4 | 1.8 | 27.04
| OPD Records |  | 13.84 |  |  |  | 0 | 1.8 | 15.64
OPD Records | Hallway |  | 25.2 |  |  |  | 0 | 0 | 25.2
| Ultrasound |  | 15.64 |  |  |  | 0 | 0 | 15.64
Ultrasound | Ultrasound CR |  | 11.8 |  |  |  | 0 | 1.8 | 13.6
| Hallway |  | 25.6 |  |  |  | 0 | 1.8 | 27.4
OPD Clinic OB-Gyne | Hallway |  | 44 |  |  |  | 0 | 2.4 | 46.4
| OPD Clinic OB-Gyne CR |  | 11.8 |  |  |  | 0 | 1.8 | 13.6
Canteen | Hallway |  | 24.12 |  |  |  | 0 | 4 | 28.12
| Dietary |  | 28.6 |  |  |  | 2.8 | 2.4 | 33.8
Dietary | Hallway |  | 98.44 |  |  |  | 0 | 6.6 | 105.04
| Supply Receiving Area |  | 21.72 |  |  |  | 0 | 1.8 | 23.52
| Dietitian Office |  | 20.8 |  |  |  | 2.8 | 1.8 | 25.4
| Dietitians Office CR |  | 12.12 |  |  |  | 0 | 0 | 12.12
| Cold Storage |  | 6.12 |  |  |  | 0 | 1.2 | 7.32
| Dry Storage |  | 16.76 |  |  |  | 0 | 1.2 | 17.96
| Garbage Disposal |  | 8 |  |  |  | 0 | 0 | 8
Supply Receiving Area | Hallway |  | 12.92 |  |  |  | 0 | 0 | 12.92
| Cold Storage |  | 5.04 |  |  |  | 0 | 0 | 5.04
Cold Storage | Dry Storage |  | 5.08 |  |  |  | 0 | 0 | 5.08
| Hallway |  | 6.8 |  |  |  | 0 | 0 | 6.8
Dry Storage | Hallway |  | 5.4 |  |  |  | 0 | 0 | 5.4
Dietitians Office | Dietitians Office CR |  | 4.92 |  |  |  | 0 | 1.6 | 6.52
Second Floor
Space | Spaces | U | A | Ti | Ti | Q | Window | Door | Wall
5 Bedward | Hallway | [5 empty] | 0 | 2.4 | 18.8
| 5 Bedward CR | [5 empty] | 0 | 1.4 | 14.8
5 Bedward CR | Hallway | [5 empty] | 0 | 0 | 5.4
5 Bedward | Hallway | [5 empty] | 0 | 2.4 | 44.8
| 5 Bedward CR | [5 empty] | 0 | 1.4 | 14.8
5 Bedward | Hallway | [7 empty] | 44.6
5 Bedward CR
5 Bedward | Hallway
5 Bedward CR
Isolation Room | Hallway
Isolation Room CR
Isolation Room CR | Hallway
Private Room | Hallway
Private Room CR
Private Room CR | Hallway
Chief of Hospital CR
Private Room | Hallway
Private Room CR
Private Room CR | Hallway
Chief Nurse | Hallway
Chief Nurse CR
Treatment Room | Hallway
Nurse Station | Dirty Utility
Hallway
Clean Linen
Nurse Station CR
Dirty Utility | Hallway
Clean Linen | Hallway
Private Room | Hallway
Private Room CR
Private Room CR | Hallway
Private Room | Hallway
Private Room CR
Private Room CR | Hallway
Isolation Room | Hallway
Isolation Room CR
Isolation Room CR | Hallway
Reception | Chief of Hospital CR
Hallway
Chief of Hospital | Hallway
Chief of Hospital CR
Conference Room | Hallway
Chief of Clinics | Hallway
Labor Room CR
Delivery Room
3 Bed Ward | 3 Bed Ward CR
Hallway
3 Bed Ward CR | Hallway
3 Bed Ward | 3 Bed Ward CR
Hallway
3 Bed Ward CR | Hallway
Elevator | Hallway
3 Bed Ward | 3 Bed Ward CR
Hallway
3 Bed Ward CR | Hallway
3 Bed Ward | 3 Bed Ward CR
Hallway
3 Bed Ward CR | Hallway
Private Room | Hallway
Private Room CR
Private Room CR | Hallway
Private Room | Hallway
Private Room CR
Private Room CR | Hallway
Private Room | Hallway
Private Room CR
Private Room CR | Hallway
Private Room | Hallway
Private Room CR
Private Room CR | Hallway
Delivery Room | Labor Room CR
Subster Room
Hallway
Subster Room | Labor Room CR
Hallway
Labor Room | Hallway
Pathologic Nursery | Hallway
Pre-mature Nursery | Hallway
Breastfeeding Room | Hallway
Pre-Operation Area
Work Area | Hallway
Pre-Operation Area
Pre Operation Area | Hallway
CSSR | Hallway
Autoclave Area CR
Sterile Supply Room
Sterile Supply Room | Recovery Room
Recovery Room | Hallway
Recovery Room CR
Major Operating Room | Hallway
Subster Room
Subster Room | Clean up Room
Hallway
Clean up Room | Hallway
Jan. Clo | Hallway
Sterile Instrument Supply | Hallway
Anesthesia Office & Storage | Hallway
DR 1 | Lounge Area
DR 2 | Lounge Area
DR 3 | Lounge Area
Lounge Area | Hallway

## References
Reference |  |  |  |  | Awning or Sliding | 2.8722
First Floor |  |  |  |  | Fixed | 2.8211 | References |  | Ground |  | Second | Third
Walls | [6 empty] | Daily Range | 8.1 | no. of changes/hr | Area (m2) | Area | no.of changes/hr | Area (m2)
Length | Area |  | Width | Length |  |  | Tdb | 34.5 | 0.264 | 37.4386 | 34.2769 | 0.264 | 34.2769
4 | 4 |  | 2 | 1 |  |  |  |  | 0.264 | 9.6512 | 2.6175 | 0.2535 | 2.6175
| 0 |  | 1.2 | 1 |  |  |  |  | 0.2535 | 7.8175 | 34.26 | 0.264 | 34.26
1.2 | 1.2 |  | 0.6 | 0.6 |  |  |  |  | 0.264 | 16.3095 | 2.6175 | 0.264 | 2.6175
0.6 | 0.36 |  | 1.2 | 0.6 |  |  |  |  | 0.2535 | 2.8375 | 220.3324 | 0.264 | 37.4087
1.2 | 0.72 |  | 1.2 | 0.6 |  |  |  |  | 0.2535 | 18.2991 | 143.2911 | 0.264 | 37.4087
1.2 | 0.72 |  | 1.6 | 1 |  |  |  |  | 0.2535 | 18.3464 | 78.7574 | 0.264 | 34.26
1.6 | 1.6 |  | 2.2 | 1 |  |  |  |  | 0.2675 | 23.3886 | 99.6547 | 0.2535 | 2.6175
4.4 | 4.4 |  | 1.2 | 0.6 |  |  |  |  | 0.2535 | 5.61 | 142.8801 | 0.264 | 34.26
| 0 |  | 2 | 1 |  |  |  |  | 0.264 | 42.1925 | 34.29 | 0.2535 | 2.6175
1.2 | 0.72 |  | 2.75 | 1 |  |  |  |  | 0.2535 | 3.7087 | 2.6175 | 0.264 | 10.1393
1.6 | 1.6 |  | 3.6 | 2.5 |  |  |  |  | 0.264 | 19.6378 | 34.1175 | 0.2535 | 2.6222
4.4 | 4.4 |  | 0.6 | 1 |  |  |  |  | 0.264 | 31.2893 | 2.6175 | 0.264 | 13.9222
8.15 | 8.15 |  | 4.2 | 1 |  |  |  |  | 0.2535 | 3.9772 | 13.6738 | 0.2535 | 2.6155
2.4 | 2.4 |  | 0.6 | 0.6 |  |  |  |  | 0.264 | 20.7487 | 2.6231 | 0.264 | 13.8738
0.6 | 0.36 |  | 0.6 | 1 |  |  |  |  | 0.264 | 17.9512 | 13.9206 | 0.2535 | 2.6186
0.6 | 0.36 |  | 1.6 | 1 |  |  |  |  | 0.264 | 18.6308 | 2.6155 | 0.264 | 30.712
2 | 2 |  | 0.6 | 0.6 |  |  |  |  | 0.264 | 17.1378 | 13.8754 | 0.2535 | 2.6374
4.8 | 4.8 |  | 4.2 | 1 |  |  |  |  | 0.264 | 11.6062 | 2.6197 | 0.264 | 17.9413
0.6 | 0.36 |  | 8.4 | 1 |  |  |  |  | 0.264 | 130.9682 | 30.712 | 0.264 | 22.829
| 0 |  | 1.4 | 1 |  |  |  |  | 0.2535 | 2.9773 | 2.6374 | 0.2535 | 2.415
4.2 | 4.2 |  | 2.4 | 1 |  |  |  |  | 0.264 | 656.179 | 17.9413 | 0.2535 | 4.7869
2.8 | 2.8 |  | 2.8 | 1 |  |  |  |  | 0.2675 | 32.86 | 22.829 | 0.2535 | 2.4581
2.8 | 1.68 |  | 1.8 | 1 |  |  |  |  | 0.264 | 12.6775 | 2.4121 | 0.264 | 13.8735
2.4 | 2.4 |  | 2.4 | 1 |  |  |  |  | 0.2535 | 3.2363 | 4.7869 | 0.2535 | 2.6175
| 0 |  | 1.73 | 1 |  |  |  |  | 0.264 | 14.3811 | 2.4581 | 0.264 | 13.8928
2.2 | 2.2 |  | 2 | 1 |  |  |  |  | 0.264 | 14.3811 | 13.8735 | 0.2535 | 2.6175
| 0 |  | 0.6 | 0.6 |  |  |  |  | 0.264 | 8.9651 | 2.6175 | 0.264 | 10.1716
0.6 | 0.36 |  | 0.6 | 0.6 |  |  |  |  | 0.264 | 14.4356 | 13.8928 | 0.2535 | 2.6213
| 0 |  | 2.4 | 1 |  |  |  |  | 0.264 | 14.4356 | 2.6175 | 0.264 | 15.8619
| 0 |  | 1.6 | 1 |  |  |  |  | 0.264 | 5.4875 | 13.7066 | 0.2535 | 2.64
14 | 14 | [7 empty] | 0.264 | 5.51 | 2.6213 | 0.264 | 15.8619
| 0 | [7 empty] | 0.264 | 5.6363 | 11.0522 | 0.2535 | 2.64
[9 empty] | 0.2535 | 5.5203 | 13.6813 | 0.264 | 24.783
Third Floor | [8 empty] | 0.264 | 9.1492 | 2.64 | 0.2535 | 2.64
Wall | [8 empty] | 0.264 | 4.9522 | 18.7319 | 0.264 | 24.8909
Doors | Windows | Wall Length | Width | Length |  |  |  |  | 0.264 | 25.2538 | 6.9296 | 0.2535 | 2.64
0 | 0 | 6.5 | 2.31 | 1 |  |  |  |  | 0.264 | 14.3811 | 25.372 | 0.264 | 13.6813
0 | 4.6 | 6 | 2.31 | 1 |  |  |  |  | 0.264 | 14.3811 | 2.6087 | 0.2535 | 2.64
0 | 4.6 | 6 | 2.31 | 1 |  |  |  |  | 0.264 | 10.418 | 6.6151 | 0.264 | 13.7512
0 | 0 | 10.23 | 2.31 | 1 |  |  |  |  | 0.264 | 9.9805 | 25.48 | 0.2535 | 2.64
0 | 0 | 17 | 2.7 | 1 |  |  |  |  | 0.264 | 14.4356 | 2.6087 | 0.264 | 16.0112
0 | 0 | 10.23 | 1.4 | 1 |  |  |  |  | 0.264 | 14.4356 | 13.7512 | 0.2535 | 2.64
0 | 4.6 | 6 | 1.4 | 1 |  |  |  |  | 0.264 | 14.3639 | 2.64 | 0.264 | 16.0112
0 | 4.6 | 6 | 1.4 | 1 |  |  |  |  | 0.264 | 8.431 | 38.4537 | 0.2535 | 2.64
0 | 0 | 6.5 | 1.4 | 1 |  |  |  |  | 0.2535 | 8.3137 | 25.372 | 0.264 | 8.9651
0 | 2.7 | 3.1 | 1.4 | 1 |  |  |  |  | 0.264 | 8.4375 | 2.6087 | 0.264 | 13.7512
0 | 1.4 | 3.7 | 3.35 | 1 |  |  |  |  | 0.264 | 13.607 | 25.48 | 0.2535 | 2.64
0 | 1.4 | 2.35 | 2.4 | 1 |  |  |  |  | 0.2535 | 17.2599 | 2.6087 | 0.264 | 13.7512
0 | 0 | 3 | 2.4 | 1 |  |  |  |  | 0.264 | 17.1267 | 13.7512 | 0.2535 | 2.64
0 | 1.4 | 3 | 2.4 | 1 |  |  |  |  | 0.264 | 8.5711 | 2.64 | 0.264 | 23.4829
0 | 1.4 | 3 | 2.23 | 1 |  |  |  |  | 0.264 | 35.3177 | 13.7512 | 0.264 | 10.7572
0 | 1.4 | 3 | 0.6 | 0.6 |  |  |  |  | 0.264 | 13.5984 | 2.64 | 0.2535 | 2.64
0 | 1.4 | 3 | 2.4 | 1 |  |  |  |  | 0.2535 | 17.0428 | 21.3616 | 0.264 | 11.315
0 | 3.35 | 3.75 | 1.2 | 0.6 |  |  |  |  | 0.264 | 10.4417 | 1.6646 | 0.2535 | 2.64
0 | 0 | 3 | 1.2 | 0.6 |  |  |  |  | 0.264 | 11.5919 | 31.4388 | 0.264 | 13.3083
0 | 2.4 | 3.9 | [6 empty] | 0.264 | 19.0769 | 34.9862 | 0.264 | 11.0872
0 | 2.4 | 3.9 | 3.35 | 1 |  |  |  |  | 0.2535 | 2.5344 | 5.4111 | 0.264 | 8.275
0 | 2.4 | 3.2 | 1.4 | 1 |  |  |  |  | 0.2535 | 34.2152 | 25.7486 | 0.264 | 13.4675
0 | 2.23 | 2.48 | 1.4 | 1 |  |  |  |  | 0.2535 | 2.5941 | 3.863 | 0.264 | 183.9438
0 | 0.6 | 1.88 | 1.4 | 1 |  |  |  |  | 0.2535 | 1.9625 | 16.7994 | 0.264 | 58.8601
0 | 0.6 | 1.5 | 1.4 | 1 |  |  |  |  | 0.264 | 5.7184 | 16.7999 | 0.2535 | 17.4452
0 | 2.4 | 5.7 | 1.4 | 1 |  |  |  |  | 0.264 | 9.225 | 10.2258 | 0.2535 | 17.4806
0 | 0 | 4.8 | 0.6 | 0.6 |  |  |  |  | 0.2535 | 1.945 | 19.0007 | 0.264 | 43.5914
0 | 1.2 | 3 | [6 empty] | 0.264 | 38.0325 | 14.9875 | 0.264 | 10.9006
0 | 1.2 | 3 | [6 empty] | 0.264 | 50.8881 | 1.68 | 0.264 | 10.7831
0 |  | 6 | [6 empty] | 0.264 | 27.0056 | 21.6006 | 0.264 | 9.4163
0 | 0 | 12 | [6 empty] | 0.2535 | 2.5344 | 23.6003 | 0.264 | 26.9958
0 | 0 | 15.4 | [6 empty] | 0.264 | 2.28 | 35.0425 | 0.2535 | 2.64
0 | 0 | 2.22 | [6 empty] | 0.2535 | 181.6992 | 5.6912 | 0.264 | 628.0183
0 | 3.33 | 3.75 | [8 empty] | 4.1338
0 | 1.4 | 3 | [8 empty] | 12.91
0 | 1.4 | 3 | [8 empty] | 7.4784
0 | 1.4 | 3 | [8 empty] | 17.5207
0 | 1.4 | 3 | [8 empty] | 2.8
0 | 0 | 2.22 | [8 empty] | 2.8
0 | 1.4 | 3.7 | [8 empty] | 2.8
0 | 0.6 | 2.35 | [8 empty] | 41.3021
5 | 0 | 3.1 | [8 empty] | 46.9742
2.0901
Note on E60: Adrian: Hallway