## Slide 1: Design of Chilled Water Type Conditioning and Ventilation System of Proposed Three Storey Hospital in Batangas
Prepared by: Abu, Mark Kervin N.
Azucena, Roniel A.
Castillo, Adrian M.

## Slide 2: Location of the Building
N
E
W
S
S
N
E
W

## Slide 3: Details of Location
13°45'21" North Latitude, 121°04'419" East Longitude
Area= 1819 m2
Outdoor Design:
Dry-Bulb Temperature = 34.5 °C
Wet-Bulb Temperature = 26.1°C
Daily Range= 8.1 °C
Design Month= May

## Slide 4: Indoor Design at 50% Relative Humidity
Dry bulb Temperature= 24 °C
Dry bulb Temperature= 22.5 °C
Dry bulb Temperature= 22 °C
Reference: Hvac Design Manual for Hospitals and Clinics, 2013 Ashrae

## Slide 5: Construction of Wall
 | R, m2 ⁰K/Watt | ρS, Kg/m2
outside air film | 0.0440 | ---
25 cement plaster | 0.0347 | 39.95
150mm CHB sand and gravel | 0.1350 | 147
25 cement plaster | 0.0347 | 39.95
inside air film | 0.12 | ---
 | RT = 1.2695 | ρST = 226 Kg/m2
 | UW = 2.7144 W/m2K | TYPE F

## Slide 6: Construction of Roof
 | R, m2K/W | ρS, Kg/m2
outside air film | 0.044 | ---
25 mm granite | 0.01375 | 42.5
200 mm concrete block, sand and gravel | 0.18 | 196
25 mm cement plaster | 0.02919 | 39.95
inside air film | 0.12 | ---
 | RT = 1.104 m2K/W | ρST = 278.45 kg/m2
 | UW = 2.58438 W/m2K | TYPE 6 roof with suspended ceiling

## Slide 7: Construction of Wall Partition
 | R, m2 ⁰K/Watt | ρS, Kg/m2
inside air film | 0.12 | ---
15 mm cement plaster | 0.0208 | 23.97
120 mm CHB sand and gravel | 0.1350 | 117.6
15 mm cement plaster | 0.0208 | 23.97
inside air film | 0.12 | ---
 | RT = 0.3896 m2K/W | ρST = 165.54 Kg/m2
 | UW = 2.5667 W/m2K | TYPE F

## Slide 8: Construction of Glass
Single glass, regular sheet with venitian blinds and light color
U= 2.8211 W/m2K (fixed)
U= 2.8722 W/m2K (awning, sliding)

## Slide 9: Load Calculation
External Wall Load
Glass Load
Roof Load
Infiltration Load
Ventilation Load
Lighting Load
Occupant Load
Partition Load
Miscellaneous Load

## Slide 10: External Wall Load Calculation
External Wall Load
𝐐𝐰 = 𝐔𝐀 𝐂𝐋𝐓𝐃𝐚𝐝𝐣
For 22⁰C, Minor Operating Room
For Area (m2)
N: 13.6 m2
For Cooling Load Temperature Difference
CLTDADJ = (CLTDSEL + LM)k + (25 – ti) + (tAV-29)
Where tav = 30.45⁰C
N: (13 – 0.55)(0.65) + (25-22) + (30.45-29)
N= 20.3425
ForHeat transfer coefficient:
U= 2.7144 W/ m2K
For Thermal Heat Load, QW (W)
QW= 2.7144 W/ m2K (13.6)(20.3425)
QW= 479.9059 W

## Slide 11: Glass Load Calculation
Glass Load
QG= QSG + QTH
QSG= (SHGF)(SC)(A)(CLF)
QTH= (U)(A)( ΔT)
For 22⁰C, Minor Operating Room
Area (m2)
N: 1.6 m2
Solar Heat Gain, QSG (W)
N: (120)(0.91)(1.6 m2)(0.55)
QSG= 96.096 W
Conduction Heat Load, QTH
N: (2.8211 W/ m2K)(1.6 m2)( 34.5 – 22) ⁰C
QTH= 56.422 W
QG= 96.096 W + 56.422 W
QG= 152.518 W

## Slide 12: Roof Load Calculation
Roof Load
QS= (U)(A)(CLTDADJ)
For 22.5⁰C, 5-Bed Ward 1
Area (m2)
34.2769 m2
Cooling Load Temperature Difference
CLTDADJ = [(CLTDMAX + LM)k + (25 – ti) + (tAV-29)]f
Where tav = 30.45⁰C
CLTDMAX= 18
k= 0.75, medium color
f= 0.75, positive ventilation

## Slide 13
CLTDADJ = [(18 + 0)0.75 + (25 – 22.5) + (30.45-29)]0.75
CLTDADJ= 13.0875
QS= 2.58438(34.2769 m2)(13.0875)
QS= 1159.35 W

## Slide 14: Infiltration Load Calculation
Infiltration Load
QS = 1.232 (L/s) (to- ti)
QL = 3000 (L/s) (ωo- ωi)
For 22°C, Minor Operating Room
Infiltration Rate, L/s
L/s = NV / 3.6
*wind speed from ASHRAE Meteo, v = 3 m/s
number of air changes, N = a +bv+ c(to – ti)
N = 0.15+(0.01)(3)+0.007(34.5-22)
N = 0.2675
volume of conditioned space, V = (floor area)(building height)
V = 23.389 m2 (4m)
V = 93.544 m3
L/s = (0.2675) (31.27) / 3.6
L/s = 6.9516

## Slide 15
For Humidity ratio of Outside Air, wo
Ho= cpT + woHg
Where:
Cp= 1.0062 kJ/kg-K
tDB = 34.5°C
hDB = h @ 34.5°C = 2564.5 kJ/kg
hWB = h @ 26.1°C = 81.2256 kJ/kg
wo =
wo= 0.018136752
For Humidity ratio of inside air, wi
wi = 0.622 RhPsat – Pt (RhPsat)
where:
Psat = P @ 22°C = 2.6431kPa
wi= 0.622(0.50) (2.6431 kPa) / 101.325 kPa – (0.50) (2.6431 kPa)
wi =0.00821976 kg/kg

## Slide 16
Sensible Heat Load (QS)
Qs= 1.232(2.2019) (34.5°C - 24 °C)
Qs= 28.4841 W
Latent Heat Load (QL)
QL= 3000 (2.2019) (0.018136752 - 0.00821976)
QL= 58.4183 W

## Slide 17: Ventilation Load
VENTILATION LOAD
QS= 1.232 (L/s) (to- ti)
QL = 3000 (L/s) (ωo- ωi)
For 24°C, Canteen
L/s = N (L/s per person)
Where L/s per person= 8
Number of occupants= 20 persons
L/s= 8(20)= 160
QS= 1.232 (160 L/s) ( 34.5 – 24)°C
Qs= 2069.76 W
QL= 3000 (160 L/s) (34.5 – 24)°C
QL= 4244.8882 W

## Slide 18: Lighting Load
Lighting Load
QS = (lamp rating)(Fu)(Fsa)(CLF)
For 24 °C, Canteen
Where:
Lamp rating= 2362.09 W
Fu=0.5
Fsa=1.2
CLF= 0.94
QS= (2362.09 W)( 0.5)( 1.2)( 0.94)
QS= 1332.219 W

## Slide 19: Occupant Load
Occupant Load
QS = (gain per person)(sensible heat gain)(no.of people)(CLF)
QL = (gain per person)(latent heat gain)(CLF)
For 24 °C, Canteen
Where:
Gain per person= 100
Sensible heat gain= 0.6
Latent heat gain= 0.4
No. of people= 20
CLF= 0.92
QS= (100)(0.6)(20)(0.92)
QS= 1104 W
QL= (100)(0.4)(0.92)
QL= 36.8 W

## Slide 20: Partition Load for Wall
Wall Partition: QS = U A ΔT
For 24 °C, Canteen
Where: Wall Partition of Canteen and Hallway
Area= 10.2 m2
ΔT= (28 - 24) °C= 4°C
QS= (2.7144)(10.2 m2) (4)
QS= 41.53032 W

## Slide 21: Partition Load for Door
For 22 °C, Minor Operating Room
Where: Door Partition of Minor Operating Room and Emergency Room
Area= 3.2 m2
ΔT= (22.5 - 22) °C= 0.5
QS= (2.3576)(3.2 m2)(0.5)
QS=37.7216 W

## Slide 22: Miscellaneous Load
For 22.5 °C, Emergency Room
Where:
W= 300.8 W
Sensible Heat Gain= 0.33
CLF= 0.96
Latent Heat Gain= 0.16
QS=(300.8 W)(0.33)(0.96)
QS= 95.29344 W
QL=(300.8 W)(0.16)(1)
QL= 48.128 W
Minor Operating Room Equipment
Smoke Detector = 0.4 W
Cardiopulmonary Bypass Machine = 150 W
Surgical Lights= 25 W
Autoclave= 2000 W
Electrosurgery= 109 W

## Slide 23: Summary of Load Calculation
SUMMARY OF HEAT LOAD CALCULATION FOR GROUND FLOOR AT 22 °C |  | 
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 1945.68192 | 0
Glass Load | 962.044 | 0
Infiltration Load | 257.4623 | 497.3868
Ventilation Load | 1309 | 2528.83296
Lighting Load | 532.87948 | 0
Occupant Load | 483 | 138
Wall Partition Load | 796.78502 | 0
Door Partition Load | 5.894 | 0
Miscellaneous Load | 723.6979 | 365.504
TOTAL | 7016.44462 | 3529.72376
OVERALL TOTAL | 10546.16838 | 
SUMMARY OF HEAT LOAD CALCULATION FOR GROUND FLOOR AT 22.5°C |  | 
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 16186.72723 | 0
Glass Load | 6662.64419 | 0
Infiltration Load | 3885.6216 | 7455.7825
Ventilation Load | 5884.032 | 11457.01248
Lighting Load | 7216.6545 | 0
Occupant Load | 4845.18 | 1713.96
Wall Partition Load | 14155.41998 | 0
Door Partition Load | 1130.043 | 0
Miscellaneous Load | 380.204326 | 1920.224
TOTAL | 60346.52683 | 22546.97898
OVERALL TOTAL | 82893.50581 | 
SUMMARY OF HEAT LOAD CALCULATION FOR GROUND FLOOR AT 24°C |  | 
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 16630.03447 | 0
Glass Load | 5175.5414 | 0
Infiltration Load | 1180.8 | 2558.912
Ventilation Load | 2069.76 | 4244.88816
Lighting Load | 2511.867 | 0
Occupant Load | 1104 | 36.8
Wall Partition Load | 3602.335 | 0
Door Partition Load | 11.986 | 0
Miscellaneous Load | 901.9296 | 455.52
TOTAL | 33188.25347 | 7296.12016
OVERALL TOTAL | 40484.37363 | 

## Slide 24: Summary of Load Calculation
SUMMARY OF HEAT LOAD CALCULATION FOR SECOND FLOOR AT 22 °C |  | 
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 2286.793008 | ___
Glass Load | 0 | ___
Infiltration Load | 406.8458102 | 787.2557721
Ventilation Load | 3757.6 | 7259.237
Lighting Load | 641.7098 | 0
Occupant Load | 3867 | 1500
Wall Partition Load | 1935.096 | 0
Door Partition Load | 110 | 0
Miscellaneous Load | 1474.13372 | 744.512
TOTAL | 14479.17834 | 10291.00477
OVERALL TOTAL | 24770.18311 | 
SUMMARY OF HEAT LOAD CALCULATION FOR SECOND FLOOR AT 22.5°C |  | 
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 18499.32996 | 0
Glass Load | 11264.605 | 0
Infiltration Load | 3339.8875 | 6560.8163
Ventilation Load | 15796.7 | 30952.7564
Lighting Load | 8698.5097 | 0
Occupant Load | 3959.9 | 4052.5
Wall Partition | 15295 | 0
Door Partition | 1021.74384 | 0
Miscellaneous Load | 1927.94243 | 973.6448
TOTAL | 79803.61843 | 42539.7175
OVERALL TOTAL | 122343.3359 | 
SUMMARY OF HEAT LOAD CALCULATION FOR SECOND FLOOR AT 24°C |  | 
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 4579.752496 | 0
Glass Load | 2949.2208 | 0
Infiltration Load | 577.8417 | 1187.028
Ventilation Load | 614.46 | 1260.2016
Lighting Load | 524.0859 | 0
Occupant Load | 938.4 | 880
Wall Partition Load | 2660.49202 | 0
Door Partition Load | 98.07616 | 0
Miscellaneous Load | 68.36544 | 34.528
TOTAL | 13010.69452 | 3361.7576
OVERALL TOTAL | 16372.45212 | 

## Slide 25: Summary of Load Calculation
SUMMARY OF HEAT LOAD CALCULATION FOR THIRD FLOOR AT 22.5°C |  | 
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 24827.88391 | 0
Roof Load | 27420.0353 | 0
Glass Load | 11472.723 | 0
Infiltration Load | 2478.26972 | 5099.36068
Ventilation Load | 13106.018 | 26381.30264
Lighting Load | 6378.502 | 0
Occupant Load | 4519.5 | 2132.1
Wall Partition Load | 11615.785 | 0
Door Partition Load | 1000.65112 | 0
Miscellaneous Load | 2157.17387 | 1089.4816
TOTAL | 104976.5419 | 34702.24492
OVERALL TOTAL | 139678.7868 | 
SUMMARY OF HEAT LOAD CALCULATION FOR THIRD FLOOR AT 24°C |  | 
HEAT SOURCES | Qs (W) | Ql (W)
External Wall | 11065.52304 | 0
Roof Load | 5910.72485 | 0
Glass Load | 436.0549 | 0
Infiltration Load | 1170.876 | 2401.36
Ventilation Load | 620.928 | 1273.4662
Lighting Load | 2460.248 | 0
Occupant Load | 0 | 0
Wall Partition Load | 3266.075 | 0
Door Partition Load | 67.89888 | 0
Miscellaneous Load | 0 | 0
TOTAL | 24998.32867 | 3674.8262
OVERALL TOTAL | 28673.15487 | 

## Slide 26: Psychrometric Method
GROUND FLOOR at 24°C initial condition;
Qs = 33188.2535 W
QL = 7296.1202 W
QT = 40484.3736 W
34.5 °CDB & 26.1 °CWB
24 °CDB & 50% RH QS = 33188.2535 QT = 40484.3736

## Slide 27: Psychrometric Method
At outdoor condition: 34.5°CDB and 26.1°CWB
Where WO = 0.018136752
Solving for PS:
P­S = 2.870882826 kPa
For the computation of enthalpy;
ho = cpTo + Wohg
ho = 1.0062(34.5°C) + 0.01813675(2564.5)
ho = 81.2256005 KJ/kg
Solving for the specific volume;
vO = 0.8963812873 m3/kg
The mass flowrate from ventilation supply:
mo = 0.1784854709 kg/s
For the properties of return air condition;
Where wi = 0.009293235
wr = 0.009289440471 kg/kgm
For the computation of enthalpy;
hr = cpTr + wrhg
hr = 1.0062(24°C) + (0.009289440471 kg/kgm)(2545.5 KJ/kg)
hr = 47.79507072 KJ/kg

## Slide 28: Psychrometric Method
For the mass flowrate from sensible heat load;
me = ma
Solving for ma:
ma = 3.141309923 kg/s
Since is less than 10% then, use 10% as the value of
mowo + mrwr = mewe
.01me (0.018136752) + 0.9me (0.009289440471) = mewe
Solving for we;
we = 0.0101741716 kga/kgv
moho + mrhr = mehe
0.1me (81.2256005) + 0.9me (47.79507072) = me(he)
Solving for he;
he = 51.1381237 KJ/kg
moto + mrtr = mete
0.1me (34.5) + 0.9me (24) = me(te)
Solving for te;
Te = 25.06°C
From psychometric chart:
TL = 11.4°C
For capacity of cooling coil;
Capacity = me (he – hL)
Capacity = 3.141309923 kg/s (51.1381237 – 32.32978727 KJ/kg)
Capacity = 59.08281386 KW

## Slide 29: Summary of A/C capacity of each Floor
Table 46 SUMMARY of A/C Capacity for each floor |  |  |  | 
FLOOR | DESIGN TEMPERATURE |  |  | 
 | 24°C | 22.5°C | 22°C | 
GROUND FLOOR | 59.0828 kW | 92.4161 kW | 17.8804 kW | 
 | 16.0086 TOR | 25.9472 TOR | 5.0844 TOR | 
SECOND FLOOR | 33.1554 kW | 160.153 kW | 38.1973 kW | 
 | 9.3089 TOR | 45.5408 TOR | 10.8617 TOR | 
THIRD FLOOR | 47.4593 kW | 159.5619 kW | ----- | 
 | 13.4954 TOR | 45.3726 TOR |  | 
 |  | TOTAL : | 607.9062 kW | 
 |  |  | 172.8627 TOR | 

## Slide 30: Equipment Selection
CHILLER CATALOGUE (CARRIER)

## Slide 31: Fan Coil Unit Catalogue (Daikin)

## Slide 32: Fan Coil Unit Catalogue (Daikin)

## Slide 33: Diffuser Catalogue (OC Water Loo)

## Slide 34: Air Handling Unit Catalogue (carrier)

## Slide 35: Ground Floor ACU Layout

## Slide 36: Second Floor ACU Layout

## Slide 37: Third Floor ACU layout

## Slide 38: Piping Calculations
Computing for L/s (Cleanup Room)
L/s=
Where cooling capacity= 3.5167 kW
V at 11.4°C = 0.001002915 m3/kg
CpWater= 4.187 kJ/kg
Tl= 25.05 °C
Te= 11.4 °C
L/s=
L/s = 0.082649003 L/s

## Slide 39: Piping Calculations
From Chiller to pump
Where Q= 19.1489 L/s
Pressure Gradient= 160.9349787 Pa/m
Length of pipe= 2m
Pressure drop= Pressure gradient x total length of pipe
Pressure drop= 321.8699574 Pa

## Slide 40: Ducting Calculations
Computing for L/s (Minor Operating Room)
L/s= Cooling Capacity(v)/ ρ*(To-Ti))
Where Cooling Capacity= 8.79175 kW
For density of air at 22°C= 1.1968 kg/
v = 0.8583 /kg
L/s=
L/s= 504.4090257 L/s

## Slide 41: Ducting Calculations
For Examination or treatment area:
Nominal Diameter= 600 mm
Velocity= 4.282 m/s
Pressure gradient= 0.324Pa/m
Equivalent Length=38.82 m
Pressure drop= 38.82m * 0.324 Pa/m
Pressure drop= 30.1537 Pa

## Slide 42: Equipment Schedule
TAG no. | Quantity | Description | Brand/Model | Capacity | No. of Indoor units connected | Electrical Data |  | 
 |  |  |  |  |  | V | ϕ | Hz
CH-1 | 1 | Air Cooled Chiller | Carrier/0700A | 668.1 kW | 96 | --- | --- | ---
TAG no. | Quantity | Description | Brand/Model | Capacity | No. of Indoor units connected | Electrical Data |  | 
 |  |  |  |  |  | V | ϕ | Hz
AHU | 1 | 39G Air Handling Unit | Carrier/Y SM-B | 668.1 kW | 15 | --- | --- | ---